## Isolated - Confirmed
Confirmed bad offset / constant flow - the short list
Objective criteria applied to all 36 meters, measured inside the confirmed water-off block (8/27 16:00-20:00 UTC). GATE: at least 1,000 samples in the block. BAD OFFSET: absolute median tofNorm above 400 counts (about 0.09 gpm) - a baseline parked off zero with no water present. CONSTANT FLOW: more than 5 gal integrated during the block AND flow present in all four hours, which rules out a transient. Three meters trip the criteria; all three trip BOTH.
Device | Lot | Classification | tofNorm median | sd | gpm equivalent | Gal in 4h block | Hours with flow | Fabricated gal/day | Register corroboration | Action
79461768 | 21 Maple Lane | BAD OFFSET + CONSTANT FLOW | -1967 | 1765 | -0.4376 | 112.9 | 4 of 4 | 677 | 4,257 gal banked 8/24-8/29 vs a 48 gal/day baseline; +688 on 8/29 and still climbing | FIELD VISIT FIRST. Replace or recal. Tenant is being billed for water that does not exist; the error grows about 690 gal every day it stays live.
70267966 | 40 Maple Lane APT #5 | BAD OFFSET + CONSTANT FLOW | 906 | 100 | 0.2016 | 48.2 | 4 of 4 | 289 | 794 gal over 8/27-8/29 against a 105 gal/day baseline - onset about 8/27 | RECAL on a verified no-flow condition. Textbook stuck offset: sd only 100 and hourly volume 11.7 / 12.0 / 12.2 / 12.3 gal. Real usage sits on top of the false floor, so do not just reset the register.
75367100 | 5033 Spruce Lane | BAD OFFSET + CONSTANT FLOW | -1786 | 1648 | -0.3973 | 5.7 | 4 of 4 | 34 | 2,664 gal 8/17-8/23 then only 375 gal 8/24-8/28; no report at all on 8/29 | RECAL or REPLACE. Dual fault: rejPct 85% means it discards most measurements and UNDER-reads real low flow, while the parked baseline still leaks about 34 gal/day of fabricated volume. This is the meter behind the under-registration complaint.
Hour-by-hour persistence inside the water-off block
Device | Lot | Hour (UTC) | Hour (EDT) | Samples | Gal in hour | % non-zero flow samples | tofNorm median | sd
79461768 | 21 Maple Lane | 16:00 | 12:00 | 3598 | 29.7 | 86.9 | -2088 | 1806
79461768 | 21 Maple Lane | 17:00 | 13:00 | 3600 | 28.7 | 86.8 | -1976 | 1801
79461768 | 21 Maple Lane | 18:00 | 14:00 | 3600 | 27.5 | 86.1 | -1946 | 1711
79461768 | 21 Maple Lane | 19:00 | 15:00 | 3600 | 27 | 86 | -1856 | 1730
70267966 | 40 Maple Lane APT #5 | 16:00 | 12:00 | 3598 | 11.7 | 100 | 869 | 154
70267966 | 40 Maple Lane APT #5 | 17:00 | 13:00 | 3600 | 12 | 99.4 | 909 | 104
70267966 | 40 Maple Lane APT #5 | 18:00 | 14:00 | 3600 | 12.2 | 100 | 912 | 32
70267966 | 40 Maple Lane APT #5 | 19:00 | 15:00 | 3600 | 12.3 | 99.9 | 924 | 58
75367100 | 5033 Spruce Lane | 16:00 | 12:00 | 2360 | 1.1 | 8.7 | -1831 | 1782
75367100 | 5033 Spruce Lane | 17:00 | 13:00 | 3600 | 0.9 | 6.1 | -1952 | 1506
75367100 | 5033 Spruce Lane | 18:00 | 14:00 | 3600 | 1.7 | 9 | -1792 | 1739
75367100 | 5033 Spruce Lane | 19:00 | 15:00 | 3600 | 1.9 | 9.4 | -1607 | 1574
How clear-cut is the cut?
There is no grey zone. The three isolated meters read 906 to 1,967 counts off zero and fabricate 5.7 to 112.9 gal during the four hours the water was off.
The worst of the 23 clean meters reads +87 counts (33 Maple) and the most any clean meter fabricates is 1.3 gal over the same four hours (144 Shady Test). Twenty of the 23 fabricate 0.0 to 0.1 gal.
That is a gap of roughly 10x on baseline offset and 40x on volume between the worst clean meter and the least-bad isolated one - the classification does not depend on where the thresholds are drawn.
10 meters could not be assessed for lack of samples in the block and are NOT cleared: 66 Shady, 83 Shady, 103 Shady, 5019 Spruce, 5013 Spruce, 76 Shady, 58 Shady, 15 Maple, 29 Maple, 40 Maple APT #3. Four of those (103 Shady, 76 Shady, 58 Shady, 15 Maple) were separately cleared on 8/29 by the quiet-period screen - see the Live Verification sheet.

## Devices of Concern
Shady Lane MHP - Devices of Concern (review COMPLETE, 36 of 36)
Final state after the complete 36-lot review (8/26-8/30): 3 faulty, 1 cycle-skipping, 5 wedges cured, 1 wedge still open, 6 watch, 22 clean. Only the 18 lots needing attention are listed here. Evidence is the 8/27 water-off block (1 Hz continuous, 14,400 samples per device) plus live re-verification on 8/29-8/30. Healthy reference: tofNorm median within +-40 counts, rejPct median 0-1, flowRate exactly 0.000 with the water off.
Severity | Device | Apartment / Lot | Category | Mechanism | Key evidence (8/27 shutoff test) | Est. gal/day | Billing direction | Recommended action
FAULTY | 79461768 | 21 Maple Lane | Phantom consumption | tofNorm noise storm (sd 1765 = 40x healthy), 87% of samples negative, rectified into forward flow. rejPct went 3% -> 79% on 8/24, the exact day the phantom began | 112.9 gal integrated with site water OFF; 22 transitions during the water-off block; 4,257 gal banked 8/24-8/29 against a 48 gal/day baseline and still accruing | 677 | OVER-billing tenant | HIGHEST PRIORITY field visit. Replace or recal. The error grows about 690 gal every day it stays live.
FAULTY | 70267966 | 40 Maple Lane APT #5 | Phantom floor | Near-total measurement rejection (rejPct 99, chronic since 8/12) combined with an offset parked +906 counts. The low sd of 25 is a few surviving samples all carrying the same wrong value, not health | 48.2 gal integrated with water OFF at a metronomic 0.202 gpm (11.7 / 12.0 / 12.2 / 12.3 gal per hour); 794 gal over 8/27-8/29 vs a 105 gal/day baseline | 289 | OVER-billing tenant | Recal on a VERIFIED no-flow condition. Real usage rides on top of the false floor, so do not simply reset the register.
FAULTY | 75367100 | 5033 Spruce Lane | Deaf meter - under-reads low flow | rejPct 83 chronic, gain railed 41, env 44, offsetAlarm + flowDirectionAlarm true. Onset 7/31 recal (env jumped to 50, gain re-committed railed) | tofNorm median -1786, sd 1648, 22 transitions during the water-off block. Registered 2,664 gal 8/17-8/23 then only 375 gal 8/24-8/28 |  | UNDER-billing | Recal or replace. THIS is the meter behind the customer complaint. Note qual reads 100 here - that indicator does not detect this fault.
CYCLE-SKIP | 77054957 | 40 Maple Lane APT #2 | Cycle-skipping; recorded volume is artefact | tofNorm quantised at exact multiples of 2024 (2024 / 4048 / 6072, plus a 41666 excursion) = correlator locking one lobe over. Healthy at rest: tnormStddev 21, rejPct 0 | Negative tofNorm rectified into POSITIVE flow, confirmed with matched pairs (+6072 and -6073 both give +1.658 gpm). Events on only 3 days in 40; lifetime 1.7 gal is essentially all artefact |  | records ~nothing | Run water inside the unit and watch the meter (lateral test). A meter this healthy seeing zero real water in 40 days is on the wrong lateral or serving an empty unit.
WEDGE-OPEN | 70269798 | 40 Maple Lane APT #3 | failedCal - FOTA cannot fix this one | failedCal true, offset 0, gain 55, L_FACTOR stuck at the 2.13 fallback. On 17040/354 since 8/26 and STILL producing zero flow records | Zero gal every day 8/18-8/30; no tofNorm since 8/5 (25-day blackout). The firmware update restored comms but did not clear the failed calibration |  | UNDER-billing | FORCED RECAL, not another FOTA. State this plainly before the rollout is assumed to sweep it up.
WEDGE-CURED | 79459895 | 83 Shady Lane | Wedged 8/7-8/30, cured by 17040/354 | Register frozen at 6645.3 for 22 days. Cured the moment 17040/354 landed 8/30 15:58 - first records 16:01 | Now gain 29 / env 35 / rejPct 0 / tnormStddev 33 - textbook healthy. BUT the register has not yet moved off 6645 | 95 | UNDER-billing (lost ~23 d) | Field draw test to confirm the register advances. Recover the outage volume for billing.
WEDGE-CURED | 79454037 | 58 Shady Lane | Wedged 7/20-8/28, cured by 17040/354 | Bruce's original catch. Now reports meterVal and tofNorm daily | Rescreened 8/29: 39,177 quiet samples, median -145, sd 71 - inside tolerance but consistently negative (~-0.032 gpm). Highest-usage lot on site | 175 | UNDER-billing (lost) | Recover the outage volume. Include in the next recal wave for the mild negative bias.
WEDGE-CURED | 79461115 | 15 Maple Lane | Wedged 8/7-8/25, cured by 17037/344 | meterVal identical (3089) for 18 days, from the moment 17028/341 landed until 17037/344 arrived 8/24 | L_FACTOR 2.255 flag WITHDRAWN - it was a 23-hour transient on 8/25-8/26 and reads 2.22 today, matching the 1/2 inch PEX standard. Offset clean (median +4, sd 77) |  | UNDER-billing (~18 d lost) | Recover the 8/7-8/25 outage volume. No L-factor change needed.
WEDGE-CURED | 75368777 | 144 Shady Lane-Old | Wedged ~8/1-8/13, cured by 17037/344 | Records every day since 8/13. Shares a pipe with 144 Test, making them a true A/B pair | The absence of usage is the separate, already-verified lot 144 finding (witness meter, 8/8) - that lateral genuinely carries no water |  | none | No action. Do not confuse the cured wedge with the dry lateral.
WEDGE-CURED | 75363901 | 75 Shady Lane | Brief wedge 7/31-8/1, self-cured | fwVerTi sat at 0 for about 26 hours, well past the 2-5 minute normal reflash, then cleared when TI v320 landed | Now among the tightest meters on site: tnormStddev 28, water-off sd 31, rejPct median 0. rsrp -123 is the second-weakest signal on site yet it reports daily |  | none | No action. Evidence that weak signal alone does not cause the wedge.
WATCH | 75368397 | 168 Shady Lane | env RATCHET - best FOTA candidate on site | env climbed monotonically 33 -> 44 over 25 days on pre-v349 17028/341, never stepping back. offset drifted 238 -> 385. gain 38 | leakSus AND offsetAlarm both fired 8/30 for the first time. The leak alarm is a FALSE POSITIVE - flow is diurnal with 46-minute idle runs and only 3.0% non-zero samples |  | degrading | FOTA to a v349+ build - the walker-decay fix addresses this exact mechanism. Do NOT escalate the leak alarm to the customer.
WATCH | 75369486 | 63 Shady Lane | Untrustworthy volume on 8/27-8/28 | rejPct hit 96 on 8/27 and 98 on 8/28 - the exact days of the tnorm jump and the +951 gal register lump | Median rejPct is only 2, so the meter is NOT chronically broken; it had two bad days. Now back to 11 |  | suspect volume | HOLD the 8/28 +951 gal out of billing pending review. I previously called it real catch-up demand - that is withdrawn.
WATCH | 75369098 | 5013 Spruce Lane | Healthy meter, ~75% reporting cadence | Register wiped 8/5, dead 8/6-8/14, healthy since. tnormStddev 22 is now among the lowest on site, rejPct 0 | GAP-CARRY TEST: every recent gap CARRIES (8/22->8/24 +165.0 vs 164.5 expected). No water is being lost today. noneventMode now reads TRUE - it accepted the attribute late |  | historical loss only | Recover ~740 gal for 8/6-8/14. NEVER difference the register across 8/5 (it would show -6,601). Residual gaps look like signal (rsrp -116).
WATCH | 75364883 | 5019 Spruce Lane | Sporadic records after a 4-day wedge | fwVerTi sat at 0 for 4 days (8/6-8/10) at FW 17021. On 17037/344 since 8/23 | Only 3 days of records in the last 16. Clean when it reports: rejPct 10, no alarms |  | reporting gaps | Push 17040/354 - it has a better record on this exact fault than 17037/344.
WATCH | 79466452 | 144 Shady Lane - Test | Degrading - noisiest of the non-faulty | tnormStddev 243, gain 44, upamp 1648, env 49 | 1.3 gal fabricated during the 4-hour water-off block - the highest of any clean meter (20 of 23 are at 0.0-0.1 gal) |  | slight OVER | Monitor. Shares a pipe with 144 Old, so the pair can be compared directly.
WATCH | 65828520 | 40 Maple Lane APT #4 | Noisy install | tnormStddev 167, upamp 1747 (third highest on site) - but rejPct 0 and no alarms | 1.2 gal fabricated during the water-off block, about 7 gal/day equivalent |  | slight OVER | Monitor; include in the next recal wave.
OCCUPANCY | 65824917 | 40 Maple Lane APT #0 | Clean meter, zero usage for 9 days | Meter is healthy: rejPct 0 (median 0, max 1 over 32 days), tnormStddev 43, no alarms | Recorded 39.5 gal 8/13-8/21 then EXACT zero for 9 straight days. The earlier usage rules out a wrong-lateral install - it has seen this unit's water |  | billing nothing | CUSTOMER QUESTION: is this unit occupied? If yes, investigate the supply. If vacant, correct the TB attributes.
RESOLVED | 79466007 | 126 Shady Lane | EXONERATED - customer-side leak, already stopped | One of the two healthy controls the whole analysis was calibrated against: tofNorm median -21, sd 39, flowRate exactly 0.000, 100% zero samples | 10,698 gal REAL leak 8/11-8/23, then zero every day 8/24-8/30. leakSus was TRUE for exactly the leak duration and cleared the day it stopped. Direction is unstable (4 changes since 8/2, latest 8/30) but that is a separate, minor issue |  | customer-side (ended) | No meter work. Customer conversation: ~10,700 gal of real consumption, now stopped.

## tofNorm Transitions
Significant tofNorm transitions - where and when
Method: tofNorm binned into 5-minute medians; a transition is logged where consecutive bin medians shift by >= 250 counts (about 5x the healthy quiet-noise sd of 39-46, or about 0.056 gpm on 3/4 inch pipe). Sorted by window, then device, then time. 8/27 window is CONFIRMED; 8/22 window is INFERRED from event-mode data - see Method sheet.
Window | Device | Apartment / Lot | Timestamp (UTC) | UTC | Local (EDT) | In shutoff? | From (counts) | To (counts) | Delta (counts) | Delta (gpm equiv) | sd before | sd after | Samples before / after
8/27 | 65823489 | 138 | 2026-08-27 11:15:00 | 11:15:00 | 07:15:00 |  | 10513 | 11988 | 1475 | 0.2604 | 3056.7 | 3718.5 | 51 / 45
8/27 | 65823489 | 138 | 2026-08-27 11:25:00 | 11:25:00 | 07:25:00 |  | 11988 | 4148.5 | -7839.5 | -1.3841 | 3718.5 | 1375.3 | 45 / 64
8/27 | 65823489 | 138 | 2026-08-27 11:45:00 | 11:45:00 | 07:45:00 |  | 4148.5 | 12463 | 8314.5 | 1.468 | 1375.3 | 3514.8 | 64 / 44
8/27 | 65823489 | 138 | 2026-08-27 12:50:00 | 12:50:00 | 08:50:00 |  | 12463 | 6338 | -6125 | -1.0814 | 3514.8 | 2641.5 | 44 / 18
8/27 | 65823489 | 138 | 2026-08-27 12:55:00 | 12:55:00 | 08:55:00 |  | 6338 | 11835 | 5497 | 0.9705 | 2641.5 | 3666.7 | 18 / 43
8/27 | 65823489 | 138 | 2026-08-27 14:15:00 | 14:15:00 | 10:15:00 |  | 11835 | 9510 | -2325 | -0.4105 | 3666.7 | 2393.4 | 43 / 57
8/27 | 65823489 | 138 | 2026-08-27 15:00:00 | 15:00:00 | 11:00:00 |  | 9510 | -41 | -9551 | -1.6863 | 2393.4 | 23.4 | 57 / 103
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 12:05:00 | 12:05:00 | 08:05:00 |  | 826 | 6469 | 5643 | 1.2554 | 780.7 | 2837.4 | 300 / 300
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 12:10:00 | 12:10:00 | 08:10:00 |  | 6469 | 807.5 | -5661.5 | -1.2595 | 2837.4 | 27.7 | 300 / 286
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 15:10:00 | 15:10:00 | 11:10:00 |  | 856 | 5751 | 4895 | 1.089 | 1878.7 | 2079.2 | 300 / 300
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 15:15:00 | 15:15:00 | 11:15:00 |  | 5751 | 865.5 | -4885.5 | -1.0869 | 2079.2 | 2463.3 | 300 / 296
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 15:30:00 | 15:30:00 | 11:30:00 |  | 855 | 5607 | 4752 | 1.0572 | 1964.8 | 104 | 300 / 47
8/27 | 70267966 | 40 Maple Lane APT #5 | 2026-08-27 15:40:00 | 15:40:00 | 11:40:00 |  | 5525 | 852 | -4673 | -1.0396 | 1118.5 | 29.5 | 219 / 300
8/27 | 75363901 | 75 Shady Lane | 2026-08-27 14:10:00 | 14:10:00 | 10:10:00 |  | -5223 | -48 | 5175 | 1.1513 | 2460.5 | 29.6 | 14 / 239
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 11:40:00 | 11:40:00 | 07:40:00 |  | -123 | 3952 | 4075 | 0.9066 | 1976.5 | 1975.7 | 6 / 31
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 12:30:00 | 12:30:00 | 08:30:00 |  | 3952 | 1135.5 | -2816.5 | -0.6266 | 1975.7 | 1732.9 | 31 / 6
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 12:50:00 | 12:50:00 | 08:50:00 |  | 1135.5 | 4706 | 3570.5 | 0.7943 | 1732.9 | 2017.6 | 6 / 84
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 12:55:00 | 12:55:00 | 08:55:00 |  | 4706 | 3970 | -736 | -0.1637 | 2017.6 | 1501.1 | 84 / 42
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 13:00:00 | 13:00:00 | 09:00:00 |  | 3970 | 19279 | 15309 | 3.4058 | 1501.1 | 3678.6 | 42 / 65
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 13:05:00 | 13:05:00 | 09:05:00 |  | 19279 | 12270.5 | -7008.5 | -1.5592 | 3678.6 | 4959.4 | 65 / 176
8/27 | 75364586 | 103 Shady Lane | 2026-08-27 13:10:00 | 13:10:00 | 09:10:00 |  | 12270.5 | 14063 | 1792.5 | 0.3988 | 4959.4 | 5958.8 | 176 / 11
8/27 | 75365427 | 132 Shady Lane | 2026-08-27 12:35:00 | 12:35:00 | 08:35:00 |  | 10538 | 10032 | -506 | -0.0893 | 3706.2 | 4471.8 | 63 / 29
8/27 | 75365427 | 132 Shady Lane | 2026-08-27 12:40:00 | 12:40:00 | 08:40:00 |  | 10032 | 5025 | -5007 | -0.884 | 4471.8 | 2721.1 | 29 / 12
8/27 | 75365427 | 132 Shady Lane | 2026-08-27 13:30:00 | 13:30:00 | 09:30:00 |  | 5025 | 8526.5 | 3501.5 | 0.6182 | 2721.1 | 2505.6 | 12 / 80
8/27 | 75365427 | 132 Shady Lane | 2026-08-27 15:10:00 | 15:10:00 | 11:10:00 |  | 8526.5 | -50.5 | -8577 | -1.5143 | 2505.6 | 39.9 | 80 / 168
8/27 | 75366029 | 148 Shady Lane | 2026-08-27 11:10:00 | 11:10:00 | 07:10:00 |  | -17359 | -2659 | 14700 | 3.2703 | 5209 | 6151.1 | 46 / 167
8/27 | 75366029 | 148 Shady Lane | 2026-08-27 11:20:00 | 11:20:00 | 07:20:00 |  | -2659 | -2370 | 289 | 0.0643 | 6151.1 | 812.1 | 167 / 78
8/27 | 75366029 | 148 Shady Lane | 2026-08-27 11:25:00 | 11:25:00 | 07:25:00 |  | -2370 | -4081 | -1711 | -0.3806 | 812.1 | 1644.2 | 78 / 21
8/27 | 75366029 | 148 Shady Lane | 2026-08-27 11:35:00 | 11:35:00 | 07:35:00 |  | -4081 | -18243 | -14162 | -3.1506 | 1644.2 | 5404.6 | 21 / 48
8/27 | 75366029 | 148 Shady Lane | 2026-08-27 14:05:00 | 14:05:00 | 10:05:00 |  | -18243 | 17 | 18260 | 4.0623 | 5404.6 | 40.2 | 48 / 141
8/27 | 75366938 | 29 Maple Lane | 2026-08-27 11:15:00 | 11:15:00 | 07:15:00 |  | 4228 | 14409.5 | 10181.5 | 2.2651 | 1605.4 | 4691.6 | 44 / 26
8/27 | 75366938 | 29 Maple Lane | 2026-08-27 11:40:00 | 11:40:00 | 07:40:00 |  | 14233 | 340 | -13893 | -3.0908 | 3418.8 | 1674 | 37 / 19
8/27 | 75366938 | 29 Maple Lane | 2026-08-27 11:45:00 | 11:45:00 | 07:45:00 |  | 340 | 2556.5 | 2216.5 | 0.4931 | 1674 | 1280.9 | 19 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 11:40:00 | 11:40:00 | 07:40:00 |  | 321 | -959.5 | -1280.5 | -0.2849 | 1672.6 | 2439.3 | 9 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 11:45:00 | 11:45:00 | 07:45:00 |  | -959.5 | 6252 | 7211.5 | 1.6043 | 2439.3 | 2710.9 | 6 / 43
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 11:50:00 | 11:50:00 | 07:50:00 |  | 6252 | 5857.5 | -394.5 | -0.0878 | 2710.9 | 2520.2 | 43 / 66
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 12:05:00 | 12:05:00 | 08:05:00 |  | 5857.5 | -833.5 | -6691 | -1.4885 | 2520.2 | 3039.3 | 66 / 10
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 12:35:00 | 12:35:00 | 08:35:00 |  | -930 | -1496 | -566 | -0.1259 | 2131.6 | 2286.6 | 6 / 11
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 12:40:00 | 12:40:00 | 08:40:00 |  | -1496 | 885.5 | 2381.5 | 0.5298 | 2286.6 | 2106.9 | 11 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 12:45:00 | 12:45:00 | 08:45:00 |  | 885.5 | 50 | -835.5 | -0.1859 | 2106.9 | 2588.1 | 6 / 26
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 13:00:00 | 13:00:00 | 09:00:00 |  | 50 | -461 | -511 | -0.1137 | 2588.1 | 1606.9 | 26 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 13:05:00 | 13:05:00 | 09:05:00 |  | -461 | 97 | 558 | 0.1241 | 1606.9 | 1354.5 | 6 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 13:45:00 | 13:45:00 | 09:45:00 |  | 97 | 5161 | 5064 | 1.1266 | 1354.5 | 2408 | 6 / 85
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:00:00 | 14:00:00 | 10:00:00 |  | 5161 | 4654 | -507 | -0.1128 | 2408 | 1888 | 85 / 109
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:05:00 | 14:05:00 | 10:05:00 |  | 4654 | 4266 | -388 | -0.0863 | 1888 | 1756.3 | 109 / 23
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:20:00 | 14:20:00 | 10:20:00 |  | 4266 | -263 | -4529 | -1.0076 | 1756.3 | 2280 | 23 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:25:00 | 14:25:00 | 10:25:00 |  | -263 | -1211 | -948 | -0.2109 | 2280 | 2748 | 6 / 9
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:45:00 | 14:45:00 | 10:45:00 |  | -1194 | -664.5 | 529.5 | 0.1178 | 1943.7 | 3189.8 | 5 / 12
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 14:50:00 | 14:50:00 | 10:50:00 |  | -664.5 | -1321 | -656.5 | -0.1461 | 3189.8 | 3299.6 | 12 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:15:00 | 15:15:00 | 11:15:00 |  | -1438.5 | -554.5 | 884 | 0.1967 | 2185.2 | 2437.7 | 6 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:25:00 | 15:25:00 | 11:25:00 |  | -554.5 | 1111 | 1665.5 | 0.3705 | 2437.7 | 2126.9 | 6 / 44
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:35:00 | 15:35:00 | 11:35:00 |  | 1111 | -972 | -2083 | -0.4634 | 2126.9 | 2793.2 | 44 / 31
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:40:00 | 15:40:00 | 11:40:00 |  | -972 | -648 | 324 | 0.0721 | 2793.2 | 2711.7 | 31 / 46
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:45:00 | 15:45:00 | 11:45:00 |  | -648 | -1200 | -552 | -0.1228 | 2711.7 | 2841.4 | 46 / 7
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:50:00 | 15:50:00 | 11:50:00 |  | -1200 | -1796 | -596 | -0.1326 | 2841.4 | 2142 | 7 / 9
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 15:55:00 | 15:55:00 | 11:55:00 |  | -1796 | -582 | 1214 | 0.2701 | 2142 | 2274.7 | 9 / 28
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 16:00:00 | 16:00:00 | 12:00:00 | YES | -582 | -954 | -372 | -0.0828 | 2274.7 | 3023.5 | 28 / 29
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 16:05:00 | 16:05:00 | 12:05:00 | YES | -954 | 400.5 | 1354.5 | 0.3013 | 3023.5 | 1722.2 | 29 / 6
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 16:20:00 | 16:20:00 | 12:20:00 | YES | 400.5 | -1720 | -2120.5 | -0.4717 | 1722.2 | 1387.1 | 6 / 225
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 16:30:00 | 16:30:00 | 12:30:00 | YES | -1691.5 | -2059.5 | -368 | -0.0819 | 1421.7 | 1673.5 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 16:45:00 | 16:45:00 | 12:45:00 | YES | -1990.5 | -1678.5 | 312 | 0.0694 | 1665.7 | 1915.5 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 17:20:00 | 17:20:00 | 13:20:00 | YES | -2167 | -1640.5 | 526.5 | 0.1171 | 1332.3 | 1540 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 17:25:00 | 17:25:00 | 13:25:00 | YES | -1640.5 | -1958 | -317.5 | -0.0706 | 1540 | 1959.7 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 17:45:00 | 17:45:00 | 13:45:00 | YES | -1801.5 | -2088 | -286.5 | -0.0637 | 1179.3 | 1195.9 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 17:50:00 | 17:50:00 | 13:50:00 | YES | -2088 | -1742.5 | 345.5 | 0.0769 | 1195.9 | 1274.2 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 18:00:00 | 18:00:00 | 14:00:00 | YES | -1988.5 | -1310.5 | 678 | 0.1508 | 1202.8 | 1731.7 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 18:05:00 | 18:05:00 | 14:05:00 | YES | -1310.5 | -1739 | -428.5 | -0.0953 | 1731.7 | 1680.1 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 18:15:00 | 18:15:00 | 14:15:00 | YES | -1816 | -2243.5 | -427.5 | -0.0951 | 1863.8 | 1706.8 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 18:30:00 | 18:30:00 | 14:30:00 | YES | -2457 | -1928 | 529 | 0.1177 | 1776.8 | 1862.3 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 18:55:00 | 18:55:00 | 14:55:00 | YES | -1756.5 | -1286 | 470.5 | 0.1047 | 1283.1 | 1409.3 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:00:00 | 19:00:00 | 15:00:00 | YES | -1286 | -1659 | -373 | -0.083 | 1409.3 | 1297.5 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:05:00 | 19:05:00 | 15:05:00 | YES | -1659 | -1348 | 311 | 0.0692 | 1297.5 | 1606.5 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:10:00 | 19:10:00 | 15:10:00 | YES | -1348 | -1818.5 | -470.5 | -0.1047 | 1606.5 | 1149.6 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:15:00 | 19:15:00 | 15:15:00 | YES | -1818.5 | -1374.5 | 444 | 0.0988 | 1149.6 | 1908.9 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:25:00 | 19:25:00 | 15:25:00 | YES | -1411.5 | -1879.5 | -468 | -0.1041 | 1566.8 | 1012.5 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:35:00 | 19:35:00 | 15:35:00 | YES | -1786.5 | -1422 | 364.5 | 0.0811 | 1904.1 | 1401.4 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:40:00 | 19:40:00 | 15:40:00 | YES | -1422 | -1723 | -301 | -0.067 | 1401.4 | 1275.9 | 300 / 300
8/27 | 75367100 | 5033 Spruce Lane | 2026-08-27 19:50:00 | 19:50:00 | 15:50:00 | YES | -1870 | -1569.5 | 300.5 | 0.0669 | 1228.2 | 2296.9 | 300 / 300
8/27 | 75368397 | 168 Shady Lane | 2026-08-27 11:50:00 | 11:50:00 | 07:50:00 |  | -4947 | -4253.5 | 693.5 | 0.1224 | 999.5 | 1219.4 | 142 / 30
8/27 | 75368397 | 168 Shady Lane | 2026-08-27 14:20:00 | 14:20:00 | 10:20:00 |  | -4415.5 | -657 | 3758.5 | 0.6636 | 773.6 | 734.6 | 130 / 6
8/27 | 75368397 | 168 Shady Lane | 2026-08-27 15:20:00 | 15:20:00 | 11:20:00 |  | -657 | -8.5 | 648.5 | 0.1145 | 734.6 | 75.6 | 6 / 46
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 11:55:00 | 11:55:00 | 07:55:00 |  | 1872.5 | 16918 | 15045.5 | 2.6563 | 3195.4 | 5614.9 | 8 / 166
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 12:00:00 | 12:00:00 | 08:00:00 |  | 16918 | 5699 | -11219 | -1.9808 | 5614.9 | 4725.3 | 166 / 228
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 12:15:00 | 12:15:00 | 08:15:00 |  | 5699 | 7381.5 | 1682.5 | 0.2971 | 4725.3 | 1926.5 | 228 / 64
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 13:00:00 | 13:00:00 | 09:00:00 |  | 7381.5 | 7867 | 485.5 | 0.0857 | 1926.5 | 2052.9 | 64 / 108
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 14:15:00 | 14:15:00 | 10:15:00 |  | 7867 | -30 | -7897 | -1.3942 | 2052.9 | 45.6 | 108 / 33
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 14:55:00 | 14:55:00 | 10:55:00 |  | 27 | 4916.5 | 4889.5 | 0.8633 | 2159.9 | 2433.1 | 300 / 300
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 15:00:00 | 15:00:00 | 11:00:00 |  | 4916.5 | 16 | -4900.5 | -0.8652 | 2433.1 | 1837.8 | 300 / 300
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 15:15:00 | 15:15:00 | 11:15:00 |  | 19.5 | 4407.5 | 4388 | 0.7747 | 1649.4 | 1086.2 | 300 / 300
8/27 | 75368439 | 44 Shady Lane | 2026-08-27 15:20:00 | 15:20:00 | 11:20:00 |  | 4407.5 | 2.5 | -4405 | -0.7777 | 1086.2 | 1201.4 | 300 / 300
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 11:40:00 | 11:40:00 | 07:40:00 |  | 10196 | 2833 | -7363 | -1.638 | 3175.6 | 1279.5 | 17 / 10
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 11:50:00 | 11:50:00 | 07:50:00 |  | 2718.5 | 1552 | -1166.5 | -0.2595 | 889.9 | 1314.9 | 32 / 7
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 12:05:00 | 12:05:00 | 08:05:00 |  | 1552 | 1054.5 | -497.5 | -0.1107 | 1314.9 | 756.8 | 7 / 44
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 12:35:00 | 12:35:00 | 08:35:00 |  | 1073 | 12815.5 | 11742.5 | 2.6123 | 245.3 | 4615.9 | 16 / 26
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 12:40:00 | 12:40:00 | 08:40:00 |  | 12815.5 | 4218.5 | -8597 | -1.9126 | 4615.9 | 1770.4 | 26 / 22
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 12:50:00 | 12:50:00 | 08:50:00 |  | 4218.5 | 4847 | 628.5 | 0.1398 | 1770.4 | 1381.1 | 22 / 23
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 12:55:00 | 12:55:00 | 08:55:00 |  | 4847 | 4247 | -600 | -0.1335 | 1381.1 | 2302.8 | 23 / 9
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 13:10:00 | 13:10:00 | 09:10:00 |  | 4247 | 9187 | 4940 | 1.099 | 2302.8 | 3901.9 | 9 / 57
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 13:20:00 | 13:20:00 | 09:20:00 |  | 9187 | 1281 | -7906 | -1.7588 | 3901.9 | 2150.4 | 57 / 17
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 13:30:00 | 13:30:00 | 09:30:00 |  | 1281 | 11380 | 10099 | 2.2467 | 2150.4 | 4114.7 | 17 / 30
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 13:55:00 | 13:55:00 | 09:55:00 |  | 11380 | 7125 | -4255 | -0.9466 | 4114.7 | 3212.4 | 30 / 29
8/27 | 75369486 | 63 Shady Lane | 2026-08-27 14:10:00 | 14:10:00 | 10:10:00 |  | 7125 | -2 | -7127 | -1.5855 | 3212.4 | 4375 | 29 / 245
8/27 | 77041962 | 40 Maple Lane APT #1 | 2026-08-27 13:35:00 | 13:35:00 | 09:35:00 |  | -10032.5 | -396 | 9636.5 | 2.1438 | 3131.9 | 1883.2 | 42 / 15
8/27 | 77041962 | 40 Maple Lane APT #1 | 2026-08-27 13:40:00 | 13:40:00 | 09:40:00 |  | -396 | -2977 | -2581 | -0.5742 | 1883.2 | 1446.7 | 15 / 39
8/27 | 77041962 | 40 Maple Lane APT #1 | 2026-08-27 13:45:00 | 13:45:00 | 09:45:00 |  | -2977 | -9658.5 | -6681.5 | -1.4864 | 1446.7 | 4530.3 | 39 / 20
8/27 | 77041962 | 40 Maple Lane APT #1 | 2026-08-27 14:25:00 | 14:25:00 | 10:25:00 |  | -9783 | 5 | 9788 | 2.1775 | 2740.1 | 18.8 | 28 / 173
8/27 | 79461115 | 15 Maple Lane | 2026-08-27 13:55:00 | 13:55:00 | 09:55:00 |  | 15839 | 6746.5 | -9092.5 | -1.6053 | 4569.7 | 1619 | 33 / 30
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 11:35:00 | 11:35:00 | 07:35:00 |  | -1533 | -1868 | -335 | -0.0745 | 1475.7 | 1420 | 281 / 297
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 11:45:00 | 11:45:00 | 07:45:00 |  | -1985 | -1719 | 266 | 0.0592 | 1339.5 | 1426.2 | 297 / 291
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 12:00:00 | 12:00:00 | 08:00:00 |  | -1496 | -1799 | -303 | -0.0674 | 1535.6 | 1464.5 | 287 / 291
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 12:10:00 | 12:10:00 | 08:10:00 |  | -1908 | -2353 | -445 | -0.099 | 1412.8 | 1486.7 | 291 / 297
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 12:30:00 | 12:30:00 | 08:30:00 |  | -2235 | -1945.5 | 289.5 | 0.0644 | 1493.2 | 1393.3 | 297 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 12:35:00 | 12:35:00 | 08:35:00 |  | -1945.5 | -1652.5 | 293 | 0.0652 | 1393.3 | 1532.4 | 300 / 298
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 12:45:00 | 12:45:00 | 08:45:00 |  | -1787 | -2195.5 | -408.5 | -0.0909 | 1576.8 | 1399 | 294 / 298
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 13:00:00 | 13:00:00 | 09:00:00 |  | -2021 | -1744 | 277 | 0.0616 | 1504.3 | 1438.2 | 295 / 297
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 13:30:00 | 13:30:00 | 09:30:00 |  | -1871 | -2262 | -391 | -0.087 | 1494.3 | 1377.1 | 291 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 13:35:00 | 13:35:00 | 09:35:00 |  | -2262 | -1772 | 490 | 0.109 | 1377.1 | 1562.1 | 300 / 281
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 13:40:00 | 13:40:00 | 09:40:00 |  | -1772 | -2036 | -264 | -0.0587 | 1562.1 | 1445.5 | 281 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 13:45:00 | 13:45:00 | 09:45:00 |  | -2036 | -1747.5 | 288.5 | 0.0642 | 1445.5 | 1425.2 | 300 / 298
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 14:10:00 | 14:10:00 | 10:10:00 |  | -1777.5 | -2282.5 | -505 | -0.1123 | 1416.3 | 1613.3 | 42 / 202
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 14:25:00 | 14:25:00 | 10:25:00 |  | -2144 | -1868 | 276 | 0.0614 | 1613.2 | 1562.5 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 14:30:00 | 14:30:00 | 10:30:00 |  | -1868 | -2244 | -376 | -0.0836 | 1562.5 | 1465.4 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 14:35:00 | 14:35:00 | 10:35:00 |  | -2244 | -1917.5 | 326.5 | 0.0726 | 1465.4 | 1641.9 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 15:05:00 | 15:05:00 | 11:05:00 |  | -2077.5 | -1757 | 320.5 | 0.0713 | 1769.8 | 1720.7 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 15:15:00 | 15:15:00 | 11:15:00 |  | -1997.5 | -2343.5 | -346 | -0.077 | 1755.4 | 1751.6 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:05:00 | 16:05:00 | 12:05:00 | YES | -2505 | -2190 | 315 | 0.0701 | 1786.5 | 1784.9 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:30:00 | 16:30:00 | 12:30:00 | YES | -2307 | -1866.5 | 440.5 | 0.098 | 1819 | 1796.3 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:40:00 | 16:40:00 | 12:40:00 | YES | -1854.5 | -2168 | -313.5 | -0.0697 | 1677.3 | 1667.4 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:45:00 | 16:45:00 | 12:45:00 | YES | -2168 | -1509 | 659 | 0.1466 | 1667.4 | 1858.9 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:50:00 | 16:50:00 | 12:50:00 | YES | -1509 | -1971.5 | -462.5 | -0.1029 | 1858.9 | 1862.3 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 16:55:00 | 16:55:00 | 12:55:00 | YES | -1971.5 | -2331.5 | -360 | -0.0801 | 1862.3 | 1813.4 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:00:00 | 17:00:00 | 13:00:00 | YES | -2331.5 | -2616 | -284.5 | -0.0633 | 1813.4 | 2015.1 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:05:00 | 17:05:00 | 13:05:00 | YES | -2616 | -2208 | 408 | 0.0908 | 2015.1 | 1879.7 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:10:00 | 17:10:00 | 13:10:00 | YES | -2208 | -1624.5 | 583.5 | 0.1298 | 1879.7 | 1860.8 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:25:00 | 17:25:00 | 13:25:00 | YES | -1633.5 | -1984.5 | -351 | -0.0781 | 1808.5 | 1595.4 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:30:00 | 17:30:00 | 13:30:00 | YES | -1984.5 | -1647.5 | 337 | 0.075 | 1595.4 | 1612.3 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:40:00 | 17:40:00 | 13:40:00 | YES | -1507 | -1876.5 | -369.5 | -0.0822 | 1626.5 | 1821.7 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:45:00 | 17:45:00 | 13:45:00 | YES | -1876.5 | -2719 | -842.5 | -0.1874 | 1821.7 | 1676 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 17:55:00 | 17:55:00 | 13:55:00 | YES | -2505.5 | -1733.5 | 772 | 0.1717 | 1708.2 | 1754.8 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 18:25:00 | 18:25:00 | 14:25:00 | YES | -1576.5 | -2178.5 | -602 | -0.1339 | 1797.6 | 1660.5 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 18:30:00 | 18:30:00 | 14:30:00 | YES | -2178.5 | -2698 | -519.5 | -0.1156 | 1660.5 | 1696.3 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 18:35:00 | 18:35:00 | 14:35:00 | YES | -2698 | -2394.5 | 303.5 | 0.0675 | 1696.3 | 1763.5 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 18:40:00 | 18:40:00 | 14:40:00 | YES | -2394.5 | -1929 | 465.5 | 0.1036 | 1763.5 | 1759.5 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 19:10:00 | 19:10:00 | 15:10:00 | YES | -1861 | -1578 | 283 | 0.063 | 1759.8 | 1851.5 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 19:20:00 | 19:20:00 | 15:20:00 | YES | -1741 | -2300.5 | -559.5 | -0.1245 | 1775 | 1765.9 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 19:35:00 | 19:35:00 | 15:35:00 | YES | -2639 | -1774.5 | 864.5 | 0.1923 | 1757.5 | 1720.1 | 300 / 300
8/27 | 79461768 | 21 Maple Lane | 2026-08-27 19:50:00 | 19:50:00 | 15:50:00 | YES | -1798 | -1501.5 | 296.5 | 0.066 | 1667.2 | 1619.9 | 300 / 300
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 11:25:00 | 11:25:00 | 07:25:00 |  | 269 | 12337 | 12068 | 2.1306 | 2276.6 | 3350.2 | 7 / 134
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 11:30:00 | 11:30:00 | 07:30:00 |  | 12337 | 11651 | -686 | -0.1211 | 3350.2 | 3684.9 | 134 / 147
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 12:45:00 | 12:45:00 | 08:45:00 |  | 11651 | 14541 | 2890 | 0.5102 | 3684.9 | 2483.8 | 147 / 61
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 12:50:00 | 12:50:00 | 08:50:00 |  | 14541 | 12294 | -2247 | -0.3967 | 2483.8 | 2989.8 | 61 / 51
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 14:40:00 | 14:40:00 | 10:40:00 |  | 12294 | -25 | -12319 | -2.175 | 2989.8 | 66.4 | 51 / 161
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 15:30:00 | 15:30:00 | 11:30:00 |  | 13 | 4094.5 | 4081.5 | 0.7206 | 66.1 | 3958.4 | 300 / 300
8/27 | 79466304 | 5027 Spruce Lane | 2026-08-27 15:35:00 | 15:35:00 | 11:35:00 |  | 4094.5 | 29 | -4065.5 | -0.7178 | 3958.4 | 65.3 | 300 / 300
8/27 | 79466379 | 106 Shady Lane | 2026-08-27 11:10:00 | 11:10:00 | 07:10:00 |  | 5108 | 11416.5 | 6308.5 | 1.4034 | 1681 | 3976.4 | 83 / 32
8/27 | 79466379 | 106 Shady Lane | 2026-08-27 12:00:00 | 12:00:00 | 08:00:00 |  | 11416.5 | 9549 | -1867.5 | -0.4155 | 3976.4 | 2845.9 | 32 / 37
8/27 | 79466379 | 106 Shady Lane | 2026-08-27 14:30:00 | 14:30:00 | 10:30:00 |  | 9549 | 7 | -9542 | -2.1228 | 2845.9 | 39.5 | 37 / 65
8/27 | 79466858 | 154 Shady Lane | 2026-08-27 13:15:00 | 13:15:00 | 09:15:00 |  | 6661 | 3450 | -3211 | -0.7143 | 1551.3 | 2062.8 | 72 / 34
8/27 | 79466858 | 154 Shady Lane | 2026-08-27 13:20:00 | 13:20:00 | 09:20:00 |  | 3450 | 4240.5 | 790.5 | 0.1759 | 2062.8 | 1899.9 | 34 / 8
8/27 | 79466858 | 154 Shady Lane | 2026-08-27 13:30:00 | 13:30:00 | 09:30:00 |  | 4240.5 | 6779.5 | 2539 | 0.5648 | 1899.9 | 1582 | 8 / 78
8/27 | 79466858 | 154 Shady Lane | 2026-08-27 14:40:00 | 14:40:00 | 10:40:00 |  | 6779.5 | 13 | -6766.5 | -1.5053 | 1582 | 46.3 | 78 / 173
8/22 | 65823489 | 138 | 2026-08-22 10:25:00 | 10:25:00 | 06:25:00 |  | 4845 | 11500.5 | 6655.5 | 1.1751 | 2217 | 4900.5 | 17 / 76
8/22 | 65823489 | 138 | 2026-08-22 11:30:00 | 11:30:00 | 07:30:00 |  | 11552 | 10763 | -789 | -0.1393 | 3003.7 | 3216.6 | 47 / 52
8/22 | 65823489 | 138 | 2026-08-22 11:50:00 | 11:50:00 | 07:50:00 |  | 10763 | 11778 | 1015 | 0.1792 | 3216.6 | 2386.8 | 52 / 47
8/22 | 65823489 | 138 | 2026-08-22 12:00:00 | 12:00:00 | 08:00:00 |  | 11778 | 6094 | -5684 | -1.0035 | 2386.8 | 1999.1 | 47 / 33
8/22 | 65823489 | 138 | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | 6094 | 12117 | 6023 | 1.0634 | 1999.1 | 3653.3 | 33 / 56
8/22 | 65823489 | 138 | 2026-08-22 20:50:00 | 20:50:00 | 16:50:00 |  | 12117 | 10734.5 | -1382.5 | -0.2441 | 3653.3 | 2727.8 | 56 / 48
8/22 | 65823489 | 138 | 2026-08-22 20:55:00 | 20:55:00 | 16:55:00 |  | 10734.5 | 11655 | 920.5 | 0.1625 | 2727.8 | 288.7 | 48 / 300
8/22 | 65823489 | 138 | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | 11655 | 10418.5 | -1236.5 | -0.2183 | 288.7 | 546.8 | 300 / 300
8/22 | 65823489 | 138 | 2026-08-22 21:05:00 | 21:05:00 | 17:05:00 |  | 10418.5 | 10759.5 | 341 | 0.0602 | 546.8 | 1338.3 | 300 / 282
8/22 | 65823489 | 138 | 2026-08-22 21:15:00 | 21:15:00 | 17:15:00 |  | 10759.5 | 3005.5 | -7754 | -1.369 | 1338.3 | 1606.5 | 282 / 10
8/22 | 65823489 | 138 | 2026-08-22 21:20:00 | 21:20:00 | 17:20:00 |  | 3005.5 | 7279 | 4273.5 | 0.7545 | 1606.5 | 3442.7 | 10 / 11
8/22 | 65823489 | 138 | 2026-08-22 21:25:00 | 21:25:00 | 17:25:00 |  | 7279 | 12029 | 4750 | 0.8386 | 3442.7 | 4596.4 | 11 / 50
8/22 | 65823489 | 138 | 2026-08-22 21:30:00 | 21:30:00 | 17:30:00 |  | 12029 | 11137 | -892 | -0.1575 | 4596.4 | 3114.2 | 50 / 45
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 10:25:00 | 10:25:00 | 06:25:00 |  | 9752 | 9480 | -272 | -0.0605 | 2929.1 | 2842.6 | 53 / 43
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 15:20:00 | 15:20:00 | 11:20:00 | YES | 9510.5 | 5585 | -3925.5 | -0.8733 | 3641.4 | 2155.1 | 58 / 23
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | 5556 | 9248.5 | 3692.5 | 0.8215 | 2434.5 | 2135.8 | 7 / 52
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 21:10:00 | 21:10:00 | 17:10:00 |  | 9084 | 4312 | -4772 | -1.0616 | 2547.1 | 1571.4 | 49 / 16
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 21:15:00 | 21:15:00 | 17:15:00 |  | 4312 | 9423 | 5111 | 1.137 | 1571.4 | 3229.7 | 16 / 53
8/22 | 65828520 | 40 Maple Lane APT #4 | 2026-08-22 21:45:00 | 21:45:00 | 17:45:00 |  | 9423 | 5507 | -3916 | -0.8712 | 3229.7 | 3255.9 | 53 / 85
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 12:00:00 | 12:00:00 | 08:00:00 |  | 4492 | 689 | -3803 | -0.8461 | 3411.1 | 1502.3 | 244 / 14
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 12:05:00 | 12:05:00 | 08:05:00 |  | 689 | 5293.5 | 4604.5 | 1.0244 | 1502.3 | 458.4 | 14 / 278
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 12:10:00 | 12:10:00 | 08:10:00 |  | 5293.5 | 5583 | 289.5 | 0.0644 | 458.4 | 622.2 | 278 / 254
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 12:45:00 | 12:45:00 | 08:45:00 |  | 5463 | 5048 | -415 | -0.0923 | 1893.1 | 1041.1 | 11 / 85
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | 5042 | 5531.5 | 489.5 | 0.1089 | 1807 | 1384.2 | 50 / 158
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 13:05:00 | 13:05:00 | 09:05:00 |  | 5610 | 6021 | 411 | 0.0914 | 2496.9 | 1499.1 | 38 / 134
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 13:20:00 | 13:20:00 | 09:20:00 |  | 5996 | 16496.5 | 10500.5 | 2.336 | 3246.9 | 1367.6 | 107 / 300
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 13:25:00 | 13:25:00 | 09:25:00 |  | 16496.5 | 4391 | -12105.5 | -2.6931 | 1367.6 | 5782.8 | 300 / 23
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 13:50:00 | 13:50:00 | 09:50:00 |  | 4391 | 5799 | 1408 | 0.3132 | 5782.8 | 1766.4 | 23 / 32
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:10:00 | 14:10:00 | 10:10:00 | YES | 5799 | 1391 | -4408 | -0.9806 | 1766.4 | 2588.1 | 32 / 23
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:15:00 | 14:15:00 | 10:15:00 | YES | 1391 | 4995 | 3604 | 0.8018 | 2588.1 | 2461.8 | 23 / 9
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:25:00 | 14:25:00 | 10:25:00 | YES | 4995 | 6014.5 | 1019.5 | 0.2268 | 2461.8 | 2460.1 | 9 / 42
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:35:00 | 14:35:00 | 10:35:00 | YES | 6244.5 | 10343.5 | 4099 | 0.9119 | 2451 | 2749.4 | 8 / 44
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:40:00 | 14:40:00 | 10:40:00 | YES | 10343.5 | 4927 | -5416.5 | -1.205 | 2749.4 | 2399.2 | 44 / 8
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 14:45:00 | 14:45:00 | 10:45:00 | YES | 4927 | 571.5 | -4355.5 | -0.969 | 2399.2 | 2630 | 8 / 6
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:05:00 | 15:05:00 | 11:05:00 | YES | 571.5 | 5881 | 5309.5 | 1.1812 | 2630 | 2640.9 | 6 / 9
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:10:00 | 15:10:00 | 11:10:00 | YES | 5881 | 4710 | -1171 | -0.2605 | 2640.9 | 2176.9 | 9 / 11
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:20:00 | 15:20:00 | 11:20:00 | YES | 4710 | 2263 | -2447 | -0.5444 | 2176.9 | 821.5 | 11 / 7
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:25:00 | 15:25:00 | 11:25:00 | YES | 2263 | 6117.5 | 3854.5 | 0.8575 | 821.5 | 2518.2 | 7 / 46
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:30:00 | 15:30:00 | 11:30:00 | YES | 6117.5 | 6475.5 | 358 | 0.0796 | 2518.2 | 573.5 | 46 / 244
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:50:00 | 15:50:00 | 11:50:00 | YES | 6243.5 | 2000.5 | -4243 | -0.9439 | 2003.2 | 1685.3 | 74 / 6
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 15:55:00 | 15:55:00 | 11:55:00 | YES | 2000.5 | 5554 | 3553.5 | 0.7905 | 1685.3 | 1941.2 | 6 / 255
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 16:10:00 | 16:10:00 | 12:10:00 | YES | 5263 | 5642 | 379 | 0.0843 | 3943.8 | 3873.3 | 64 / 151
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 16:15:00 | 16:15:00 | 12:15:00 | YES | 5642 | 4378.5 | -1263.5 | -0.2811 | 3873.3 | 2007.8 | 151 / 52
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 16:20:00 | 16:20:00 | 12:20:00 | YES | 4378.5 | 10599 | 6220.5 | 1.3839 | 2007.8 | 4244.6 | 52 / 25
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 16:25:00 | 16:25:00 | 12:25:00 | YES | 10599 | 13247 | 2648 | 0.5891 | 4244.6 | 4126.8 | 25 / 40
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 17:00:00 | 17:00:00 | 13:00:00 | YES | 13247 | 5299 | -7948 | -1.7682 | 4126.8 | 1211.8 | 40 / 65
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 17:05:00 | 17:05:00 | 13:05:00 | YES | 5299 | 4235 | -1064 | -0.2367 | 1211.8 | 635.3 | 65 / 135
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 17:35:00 | 17:35:00 | 13:35:00 |  | 4048 | 5066 | 1018 | 0.2265 | 1185.6 | 1490.1 | 23 / 89
8/22 | 70267966 | 40 Maple Lane APT #5 | 2026-08-22 17:40:00 | 17:40:00 | 13:40:00 |  | 5066 | 4720 | -346 | -0.077 | 1490.1 | 2038.2 | 89 / 11
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 10:15:00 | 10:15:00 | 06:15:00 |  | -3223 | -5436 | -2213 | -0.4923 | 3657.4 | 2641.2 | 19 / 7
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 11:55:00 | 11:55:00 | 07:55:00 |  | -5436 | -452.5 | 4983.5 | 1.1087 | 2641.2 | 4777.8 | 7 / 6
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 12:15:00 | 12:15:00 | 08:15:00 |  | -452.5 | -4897 | -4444.5 | -0.9888 | 4777.8 | 2440.6 | 6 / 9
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | -4897 | -6655.5 | -1758.5 | -0.3912 | 2440.6 | 5648.7 | 9 / 8
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | -6655.5 | -843.5 | 5812 | 1.293 | 5648.7 | 3293.5 | 8 / 8
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | -843.5 | -6288 | -5444.5 | -1.2112 | 3293.5 | 4696.7 | 8 / 19
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | -6288 | -131 | 6157 | 1.3697 | 4696.7 | 3972.4 | 19 / 7
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 20:00:00 | 20:00:00 | 16:00:00 |  | -131 | -6391 | -6260 | -1.3927 | 3972.4 | 2696.2 | 7 / 37
8/22 | 70268832 | 116 Shady Lane | 2026-08-22 21:30:00 | 21:30:00 | 17:30:00 |  | -6391 | -4916.5 | 1474.5 | 0.328 | 2696.2 | 5519.2 | 37 / 6
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 10:40:00 | 10:40:00 | 06:40:00 |  | -26 | -9462.5 | -9436.5 | -2.0993 | 1532.7 | 4018.8 | 6 / 12
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 11:50:00 | 11:50:00 | 07:50:00 |  | -9692 | -9009.5 | 682.5 | 0.1518 | 2760.6 | 3765.1 | 29 / 10
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 12:05:00 | 12:05:00 | 08:05:00 |  | -9212.5 | -4192 | 5020.5 | 1.1169 | 2378.9 | 1265.2 | 32 / 131
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 12:10:00 | 12:10:00 | 08:10:00 |  | -4192 | -3045 | 1147 | 0.2552 | 1265.2 | 1089.4 | 131 / 74
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 12:20:00 | 12:20:00 | 08:20:00 |  | -3049.5 | -549 | 2500.5 | 0.5563 | 773.2 | 1006 | 58 / 8
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 12:30:00 | 12:30:00 | 08:30:00 |  | -549 | -3024 | -2475 | -0.5506 | 1006 | 745.8 | 8 / 58
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | -2984 | 654.5 | 3638.5 | 0.8095 | 745.9 | 1790 | 59 / 6
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 13:00:00 | 13:00:00 | 09:00:00 |  | 654.5 | -4876 | -5530.5 | -1.2304 | 1790 | 1721.9 | 6 / 49
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 13:30:00 | 13:30:00 | 09:30:00 |  | -4884 | -3007 | 1877 | 0.4176 | 5471.2 | 768.1 | 91 / 66
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 14:00:00 | 14:00:00 | 10:00:00 | YES | -3035 | -3953 | -918 | -0.2042 | 756.8 | 1794.5 | 66 / 35
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 17:40:00 | 17:40:00 | 13:40:00 |  | -3953 | -881 | 3072 | 0.6834 | 1794.5 | 3001.8 | 35 / 21
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | -881 | -3911 | -3030 | -0.6741 | 3001.8 | 2819.1 | 21 / 109
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | -3911 | -4516 | -605 | -0.1346 | 2819.1 | 4077 | 109 / 47
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | -4516 | -1064 | 3452 | 0.768 | 4077 | 1228.3 | 47 / 5
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | -1064 | -4120 | -3056 | -0.6799 | 1228.3 | 1271.3 | 5 / 50
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 18:20:00 | 18:20:00 | 14:20:00 |  | -4198 | -1164 | 3034 | 0.675 | 1268.5 | 1476.4 | 56 / 10
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 18:45:00 | 18:45:00 | 14:45:00 |  | -1164 | -34 | 1130 | 0.2514 | 1476.4 | 2070.1 | 10 / 5
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 19:15:00 | 19:15:00 | 15:15:00 |  | -34 | -3256 | -3222 | -0.7168 | 2070.1 | 2146.6 | 5 / 21
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 19:20:00 | 19:20:00 | 15:20:00 |  | -3256 | 91.5 | 3347.5 | 0.7447 | 2146.6 | 1630.1 | 21 / 12
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 20:05:00 | 20:05:00 | 16:05:00 |  | 91.5 | -4390 | -4481.5 | -0.997 | 1630.1 | 2367.1 | 12 / 13
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 20:40:00 | 20:40:00 | 16:40:00 |  | -4037 | -4574 | -537 | -0.1195 | 1845.4 | 1733.3 | 63 / 23
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 20:55:00 | 20:55:00 | 16:55:00 |  | -4574 | -4117 | 457 | 0.1017 | 1733.3 | 1845.7 | 23 / 40
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | -4117 | -4701.5 | -584.5 | -0.13 | 1845.7 | 1814.3 | 40 / 22
8/22 | 75362887 | 66 Shady Lane | 2026-08-22 21:10:00 | 21:10:00 | 17:10:00 |  | -4701.5 | -3097 | 1604.5 | 0.357 | 1814.3 | 1525.8 | 22 / 87
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 12:00:00 | 12:00:00 | 08:00:00 |  | -5004.5 | -4663.5 | 341 | 0.0759 | 2228.7 | 1851.1 | 148 / 20
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 13:50:00 | 13:50:00 | 09:50:00 |  | -4663.5 | -758 | 3905.5 | 0.8689 | 1851.1 | 1810 | 20 / 8
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 14:15:00 | 14:15:00 | 10:15:00 | YES | -758 | -4538 | -3780 | -0.8409 | 1810 | 2099.9 | 8 / 12
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 14:30:00 | 14:30:00 | 10:30:00 | YES | -4538 | -4021 | 517 | 0.115 | 2099.9 | 676.5 | 12 / 74
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 14:40:00 | 14:40:00 | 10:40:00 | YES | -4021 | -4950.5 | -929.5 | -0.2068 | 676.5 | 1004.2 | 74 / 46
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 14:55:00 | 14:55:00 | 10:55:00 | YES | -4630 | -3676 | 954 | 0.2122 | 1772.9 | 1091.9 | 97 / 14
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 17:35:00 | 17:35:00 | 13:35:00 |  | -3676 | -494 | 3182 | 0.7079 | 1091.9 | 2758.6 | 14 / 6
8/22 | 75363901 | 75 Shady Lane | 2026-08-22 19:40:00 | 19:40:00 | 15:40:00 |  | -494 | -3908 | -3414 | -0.7595 | 2758.6 | 437.3 | 6 / 81
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 10:25:00 | 10:25:00 | 06:25:00 |  | 7138 | 10458 | 3320 | 0.5862 | 1483.2 | 2951 | 255 / 81
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 12:10:00 | 12:10:00 | 08:10:00 |  | 10458 | 11203 | 745 | 0.1315 | 2951 | 2865.8 | 81 / 75
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 13:50:00 | 13:50:00 | 09:50:00 |  | 11203 | 7409 | -3794 | -0.6698 | 2865.8 | 1502.2 | 75 / 41
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 13:55:00 | 13:55:00 | 09:55:00 |  | 7409 | 6781.5 | -627.5 | -0.1108 | 1502.2 | 2598.8 | 41 / 86
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 14:10:00 | 14:10:00 | 10:10:00 | YES | 6562.5 | 6086 | -476.5 | -0.0841 | 1567.3 | 2670.3 | 56 / 268
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 14:15:00 | 14:15:00 | 10:15:00 | YES | 6086 | 7790 | 1704 | 0.3008 | 2670.3 | 3118.9 | 268 / 20
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | 7790 | 7364 | -426 | -0.0752 | 3118.9 | 2310.2 | 20 / 85
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | 7364 | 3257 | -4107 | -0.7251 | 2310.2 | 1136 | 85 / 9
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | 3257 | 4112 | 855 | 0.151 | 1136 | 1683.4 | 9 / 68
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:15:00 | 18:15:00 | 14:15:00 |  | 4112 | 7427 | 3315 | 0.5853 | 1683.4 | 2724.4 | 68 / 78
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:25:00 | 18:25:00 | 14:25:00 |  | 7243 | 6753 | -490 | -0.0865 | 2242.8 | 1715.5 | 84 / 208
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:30:00 | 18:30:00 | 14:30:00 |  | 6753 | 21344.5 | 14591.5 | 2.5762 | 1715.5 | 8519.7 | 208 / 16
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:35:00 | 18:35:00 | 14:35:00 |  | 21344.5 | 7050.5 | -14294 | -2.5237 | 8519.7 | 2734.2 | 16 / 44
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:50:00 | 18:50:00 | 14:50:00 |  | 6867 | 687 | -6180 | -1.0911 | 2668.9 | 3180.7 | 76 / 19
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 18:55:00 | 18:55:00 | 14:55:00 |  | 687 | 4281 | 3594 | 0.6345 | 3180.7 | 1052.3 | 19 / 43
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 19:00:00 | 19:00:00 | 15:00:00 |  | 4281 | 5728 | 1447 | 0.2555 | 1052.3 | 6802.8 | 43 / 55
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 19:05:00 | 19:05:00 | 15:05:00 |  | 5728 | 8251 | 2523 | 0.4454 | 6802.8 | 3331.4 | 55 / 87
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 19:10:00 | 19:10:00 | 15:10:00 |  | 8251 | 7365 | -886 | -0.1564 | 3331.4 | 2426.5 | 87 / 209
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 19:30:00 | 19:30:00 | 15:30:00 |  | 7366 | 17642 | 10276 | 1.8143 | 1825 | 7818.8 | 105 / 16
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 19:50:00 | 19:50:00 | 15:50:00 |  | 17642 | 8282 | -9360 | -1.6525 | 7818.8 | 3058.4 | 16 / 208
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 20:05:00 | 20:05:00 | 16:05:00 |  | 8196 | 4326.5 | -3869.5 | -0.6832 | 829.1 | 2070 | 238 / 24
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 20:35:00 | 20:35:00 | 16:35:00 |  | 4151 | 3789 | -362 | -0.0639 | 1712.2 | 1897.5 | 73 / 12
8/22 | 75363992 | 84 Shady Lane | 2026-08-22 20:45:00 | 20:45:00 | 16:45:00 |  | 3789 | 11997.5 | 8208.5 | 1.4492 | 1897.5 | 2632 | 12 / 44
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 10:25:00 | 10:25:00 | 06:25:00 |  | 3280 | 2295 | -985 | -0.2191 | 1537.7 | 1078.2 | 31 / 7
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 11:15:00 | 11:15:00 | 07:15:00 |  | 2295 | 4350 | 2055 | 0.4572 | 1078.2 | 2121.8 | 7 / 13
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 11:25:00 | 11:25:00 | 07:25:00 |  | 4350 | 3565 | -785 | -0.1746 | 2121.8 | 1653.2 | 13 / 20
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 11:45:00 | 11:45:00 | 07:45:00 |  | 3565 | 5272 | 1707 | 0.3798 | 1653.2 | 2212.5 | 20 / 78
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | 5272 | 10774 | 5502 | 1.224 | 2212.5 | 6089.6 | 78 / 23
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 13:00:00 | 13:00:00 | 09:00:00 |  | 10774 | 4917 | -5857 | -1.303 | 6089.6 | 2561.1 | 23 / 17
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 13:05:00 | 13:05:00 | 09:05:00 |  | 4917 | 2823.5 | -2093.5 | -0.4657 | 2561.1 | 2056.3 | 17 / 8
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 13:55:00 | 13:55:00 | 09:55:00 |  | 2823.5 | 67 | -2756.5 | -0.6132 | 2056.3 | 2485.9 | 8 / 7
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 14:00:00 | 14:00:00 | 10:00:00 | YES | 67 | 3945 | 3878 | 0.8627 | 2485.9 | 1443.3 | 7 / 27
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | 3945 | 311 | -3634 | -0.8085 | 1443.3 | 4660.5 | 27 / 7
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 18:40:00 | 18:40:00 | 14:40:00 |  | 311 | 4724.5 | 4413.5 | 0.9819 | 4660.5 | 1212.9 | 7 / 30
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 18:45:00 | 18:45:00 | 14:45:00 |  | 4724.5 | 1101.5 | -3623 | -0.806 | 1212.9 | 2139.7 | 30 / 6
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 18:50:00 | 18:50:00 | 14:50:00 |  | 1101.5 | 4820 | 3718.5 | 0.8273 | 2139.7 | 2218.7 | 6 / 75
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 19:30:00 | 19:30:00 | 15:30:00 |  | 4820 | 5076 | 256 | 0.057 | 2218.7 | 2104.8 | 75 / 47
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 19:35:00 | 19:35:00 | 15:35:00 |  | 5076 | 4465 | -611 | -0.1359 | 2104.8 | 2292.3 | 47 / 23
8/22 | 75364586 | 103 Shady Lane | 2026-08-22 21:20:00 | 21:20:00 | 17:20:00 |  | 4465 | 4738 | 273 | 0.0607 | 2292.3 | 2343.9 | 23 / 12
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 13:05:00 | 13:05:00 | 09:05:00 |  | 10024 | 7169 | -2855 | -0.5041 | 3358.9 | 2051 | 73 / 42
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 13:10:00 | 13:10:00 | 09:10:00 |  | 7169 | 6863 | -306 | -0.054 | 2051 | 3356.4 | 42 / 12
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 13:30:00 | 13:30:00 | 09:30:00 |  | 6863 | 5760 | -1103 | -0.1947 | 3356.4 | 2441.5 | 12 / 16
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 13:40:00 | 13:40:00 | 09:40:00 |  | 5760 | 9526.5 | 3766.5 | 0.665 | 2441.5 | 3106.4 | 16 / 76
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | 9526.5 | 10120 | 593.5 | 0.1048 | 3106.4 | 3734.3 | 76 / 17
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 19:55:00 | 19:55:00 | 15:55:00 |  | 10020.5 | 10728.5 | 708 | 0.125 | 3011.4 | 2404.1 | 56 / 38
8/22 | 75365427 | 132 Shady Lane | 2026-08-22 20:30:00 | 20:30:00 | 16:30:00 |  | 10702 | 6615.5 | -4086.5 | -0.7215 | 4489.5 | 3052.5 | 35 / 14
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 11:00:00 | 11:00:00 | 07:00:00 |  | -7432.5 | -5117 | 2315.5 | 0.5151 | 2389.1 | 320.4 | 102 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 11:10:00 | 11:10:00 | 07:10:00 |  | -5251 | -1784 | 3467 | 0.7713 | 936.5 | 1172.7 | 139 / 9
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 11:40:00 | 11:40:00 | 07:40:00 |  | -1784 | -8768 | -6984 | -1.5537 | 1172.7 | 3362.6 | 9 / 50
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | -8768 | -5588.5 | 3179.5 | 0.7073 | 3362.6 | 2411.1 | 50 / 14
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | -5588.5 | -4957 | 631.5 | 0.1405 | 2411.1 | 287.1 | 14 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | -4957 | -4697.5 | 259.5 | 0.0577 | 287.1 | 216.1 | 300 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | -4697.5 | -5284.5 | -587 | -0.1306 | 216.1 | 328.6 | 300 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 18:15:00 | 18:15:00 | 14:15:00 |  | -5101.5 | -4787.5 | 314 | 0.0699 | 326.6 | 300.6 | 300 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 18:20:00 | 18:20:00 | 14:20:00 |  | -4787.5 | -5318.5 | -531 | -0.1181 | 300.6 | 362.4 | 300 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 18:25:00 | 18:25:00 | 14:25:00 |  | -5318.5 | -4733 | 585.5 | 0.1303 | 362.4 | 235 | 300 / 300
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 20:40:00 | 20:40:00 | 16:40:00 |  | -4871.5 | -4504 | 367.5 | 0.0818 | 570 | 1150.3 | 208 / 18
8/22 | 75365898 | 136 Shady Lane | 2026-08-22 20:50:00 | 20:50:00 | 16:50:00 |  | -4351 | -7167 | -2816 | -0.6265 | 445.5 | 1949.1 | 285 / 99
8/22 | 75366011 | 96 Shady Lane | 2026-08-22 18:55:00 | 18:55:00 | 14:55:00 |  | 10007.5 | 6707 | -3300.5 | -0.7343 | 4191.2 | 2792.2 | 38 / 79
8/22 | 75366011 | 96 Shady Lane | 2026-08-22 19:25:00 | 19:25:00 | 15:25:00 |  | 6707 | 10402 | 3695 | 0.822 | 2792.2 | 3224.2 | 79 / 39
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:30:00 | 13:30:00 | 09:30:00 |  | -15875 | -4405 | 11470 | 2.5517 | 4809.8 | 2323.7 | 51 / 220
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:35:00 | 13:35:00 | 09:35:00 |  | -4405 | -4850.5 | -445.5 | -0.0991 | 2323.7 | 214.4 | 220 / 300
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:40:00 | 13:40:00 | 09:40:00 |  | -4850.5 | -5202.5 | -352 | -0.0783 | 214.4 | 197.6 | 300 / 300
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:45:00 | 13:45:00 | 09:45:00 |  | -5202.5 | -5674 | -471.5 | -0.1049 | 197.6 | 5429.3 | 300 / 199
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:50:00 | 13:50:00 | 09:50:00 |  | -5674 | -4828.5 | 845.5 | 0.1881 | 5429.3 | 438.2 | 199 / 300
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 13:55:00 | 13:55:00 | 09:55:00 |  | -4828.5 | -2203.5 | 2625 | 0.584 | 438.2 | 1742.1 | 300 / 22
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 14:30:00 | 14:30:00 | 10:30:00 | YES | -2213 | -2529 | -316 | -0.0703 | 465.5 | 6159.2 | 126 / 89
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 14:35:00 | 14:35:00 | 10:35:00 | YES | -2529 | -13188 | -10659 | -2.3713 | 6159.2 | 4749.6 | 89 / 29
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | -13188 | -438.5 | 12749.5 | 2.8364 | 4749.6 | 1432.7 | 29 / 6
8/22 | 75366029 | 148 Shady Lane | 2026-08-22 19:05:00 | 19:05:00 | 15:05:00 |  | -438.5 | -14808.5 | -14370 | -3.1969 | 1432.7 | 4880.4 | 6 / 54
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 12:10:00 | 12:10:00 | 08:10:00 |  | 233 | 3524.5 | 3291.5 | 0.7323 | 1113.2 | 2295.7 | 5 / 22
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 12:15:00 | 12:15:00 | 08:15:00 |  | 3524.5 | 2252.5 | -1272 | -0.283 | 2295.7 | 2073.1 | 22 / 140
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 12:20:00 | 12:20:00 | 08:20:00 |  | 2252.5 | 1649 | -603.5 | -0.1343 | 2073.1 | 1454.2 | 140 / 21
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | 1649 | 14065 | 12416 | 2.7622 | 1454.2 | 5143 | 21 / 32
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 13:15:00 | 13:15:00 | 09:15:00 |  | 14065 | 1299 | -12766 | -2.84 | 5143 | 1667.1 | 32 / 61
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 13:20:00 | 13:20:00 | 09:20:00 |  | 1299 | 4308.5 | 3009.5 | 0.6695 | 1667.1 | 1615.5 | 61 / 14
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 14:45:00 | 14:45:00 | 10:45:00 | YES | 4308.5 | 2120 | -2188.5 | -0.4869 | 1615.5 | 2366.9 | 14 / 9
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 14:50:00 | 14:50:00 | 10:50:00 | YES | 2120 | 3851 | 1731 | 0.3851 | 2366.9 | 1714.2 | 9 / 25
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 19:10:00 | 19:10:00 | 15:10:00 |  | 3851 | 1647 | -2204 | -0.4903 | 1714.2 | 2087.3 | 25 / 7
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 20:20:00 | 20:20:00 | 16:20:00 |  | 1647 | 12993 | 11346 | 2.5241 | 2087.3 | 2641.7 | 7 / 18
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 20:25:00 | 20:25:00 | 16:25:00 |  | 12993 | 12728 | -265 | -0.059 | 2641.7 | 5175.2 | 18 / 33
8/22 | 75366938 | 29 Maple Lane | 2026-08-22 21:40:00 | 21:40:00 | 17:40:00 |  | 12728 | 3344 | -9384 | -2.0877 | 5175.2 | 1925.3 | 33 / 9
8/22 | 75366953 | 152 Shady Lane | 2026-08-22 13:00:00 | 13:00:00 | 09:00:00 |  | 8447 | 10386 | 1939 | 0.4314 | 4870 | 2992.5 | 11 / 46
8/22 | 75366953 | 152 Shady Lane | 2026-08-22 18:20:00 | 18:20:00 | 14:20:00 |  | 10386 | 2202 | -8184 | -1.8207 | 2992.5 | 8352.7 | 46 / 8
8/22 | 75366953 | 152 Shady Lane | 2026-08-22 19:50:00 | 19:50:00 | 15:50:00 |  | 2202 | 10300 | 8098 | 1.8016 | 8352.7 | 3188 | 8 / 39
8/22 | 75366953 | 152 Shady Lane | 2026-08-22 20:00:00 | 20:00:00 | 16:00:00 |  | 10300 | 10677 | 377 | 0.0839 | 3188 | 3711.8 | 39 / 55
8/22 | 75366953 | 152 Shady Lane | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | 10677 | 10059 | -618 | -0.1375 | 3711.8 | 1284.4 | 55 / 139
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 10:55:00 | 10:55:00 | 06:55:00 |  | -4710 | -4282.5 | 427.5 | 0.0755 | 1370.7 | 769.8 | 187 / 120
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 11:20:00 | 11:20:00 | 07:20:00 |  | -4282.5 | -4541.5 | -259 | -0.0457 | 769.8 | 581.2 | 120 / 122
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 12:10:00 | 12:10:00 | 08:10:00 |  | -4485 | -3395.5 | 1089.5 | 0.1924 | 554.7 | 1156.6 | 149 / 24
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 12:25:00 | 12:25:00 | 08:25:00 |  | -3395.5 | -4914 | -1518.5 | -0.2681 | 1156.6 | 854.6 | 24 / 60
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 12:30:00 | 12:30:00 | 08:30:00 |  | -4914 | -4551 | 363 | 0.0641 | 854.6 | 1009.6 | 60 / 47
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 13:25:00 | 13:25:00 | 09:25:00 |  | -4674 | -3795 | 879 | 0.1552 | 850.6 | 356.9 | 121 / 149
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 13:30:00 | 13:30:00 | 09:30:00 |  | -3795 | -2519 | 1276 | 0.2253 | 356.9 | 1304.8 | 149 / 47
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 13:35:00 | 13:35:00 | 09:35:00 |  | -2519 | -3149 | -630 | -0.1112 | 1304.8 | 1575 | 47 / 141
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 13:50:00 | 13:50:00 | 09:50:00 |  | -3157 | -4693 | -1536 | -0.2712 | 1574.9 | 632.8 | 34 / 121
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 14:15:00 | 14:15:00 | 10:15:00 | YES | -4693 | -4100 | 593 | 0.1047 | 632.8 | 1746.8 | 121 / 14
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | -4100 | -4716 | -616 | -0.1088 | 1746.8 | 998 | 14 / 56
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | -4950 | -2469 | 2481 | 0.438 | 737.2 | 1298.1 | 113 / 29
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | -2469 | -4933 | -2464 | -0.435 | 1298.1 | 1276.1 | 29 / 107
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 18:30:00 | 18:30:00 | 14:30:00 |  | -4933 | -3311 | 1622 | 0.2864 | 1276.1 | 1385.7 | 107 / 13
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 18:55:00 | 18:55:00 | 14:55:00 |  | -3311 | -5152 | -1841 | -0.325 | 1385.7 | 848.9 | 13 / 114
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 19:05:00 | 19:05:00 | 15:05:00 |  | -5152 | -4687.5 | 464.5 | 0.082 | 848.9 | 786 | 114 / 126
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 19:10:00 | 19:10:00 | 15:10:00 |  | -4687.5 | -2957 | 1730.5 | 0.3055 | 786 | 1086.4 | 126 / 20
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 19:35:00 | 19:35:00 | 15:35:00 |  | -2957 | -4805 | -1848 | -0.3263 | 1086.4 | 953.2 | 20 / 120
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 19:40:00 | 19:40:00 | 15:40:00 |  | -4805 | -1324 | 3481 | 0.6146 | 953.2 | 1112.1 | 120 / 5
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 19:50:00 | 19:50:00 | 15:50:00 |  | -1324 | -2705.5 | -1381.5 | -0.2439 | 1112.1 | 1654.3 | 5 / 22
8/22 | 75368397 | 168 Shady Lane | 2026-08-22 20:25:00 | 20:25:00 | 16:25:00 |  | -2705.5 | -4605.5 | -1900 | -0.3355 | 1654.3 | 536.7 | 22 / 164
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 11:25:00 | 11:25:00 | 07:25:00 |  | 8809.5 | 8075 | -734.5 | -0.1297 | 2797 | 2011.6 | 44 / 67
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 13:10:00 | 13:10:00 | 09:10:00 |  | 8075 | 8716 | 641 | 0.1132 | 2011.6 | 2849.4 | 67 / 39
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 13:55:00 | 13:55:00 | 09:55:00 |  | 8716 | 5684.5 | -3031.5 | -0.5352 | 2849.4 | 1665.2 | 39 / 50
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 17:35:00 | 17:35:00 | 13:35:00 |  | 5684.5 | 8889 | 3204.5 | 0.5658 | 1665.2 | 3950.1 | 50 / 59
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 21:35:00 | 21:35:00 | 17:35:00 |  | 8889 | 7432 | -1457 | -0.2572 | 3950.1 | 2080.3 | 59 / 45
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 21:40:00 | 21:40:00 | 17:40:00 |  | 7432 | 21186 | 13754 | 2.4283 | 2080.3 | 7756.4 | 45 / 13
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 21:45:00 | 21:45:00 | 17:45:00 |  | 21186 | 10247 | -10939 | -1.9313 | 7756.4 | 5873.4 | 13 / 253
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 21:50:00 | 21:50:00 | 17:50:00 |  | 10247 | 13792.5 | 3545.5 | 0.626 | 5873.4 | 5998.1 | 253 / 114
8/22 | 75368439 | 44 Shady Lane | 2026-08-22 21:55:00 | 21:55:00 | 17:55:00 |  | 13792.5 | 13050.5 | -742 | -0.131 | 5998.1 | 7312.8 | 114 / 44
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 17:30:00 | 17:30:00 | 13:30:00 |  | 4512.5 | 18718.5 | 14206 | 3.1604 | 2348.6 | 5323.9 | 6 / 76
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 17:35:00 | 17:35:00 | 13:35:00 |  | 18718.5 | 6912 | -11806.5 | -2.6266 | 5323.9 | 2282.8 | 76 / 291
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | 7093 | 7650 | 557 | 0.1239 | 1866.8 | 1241.3 | 300 / 95
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | 7650 | 9581 | 1931 | 0.4296 | 1241.3 | 2961.4 | 95 / 38
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | 9581 | 14783.5 | 5202.5 | 1.1574 | 2961.4 | 3725.6 | 38 / 160
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:10:00 | 18:10:00 | 14:10:00 |  | 14783.5 | 13408 | -1375.5 | -0.306 | 3725.6 | 1623.4 | 160 / 164
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:15:00 | 18:15:00 | 14:15:00 |  | 13408 | 14979 | 1571 | 0.3495 | 1623.4 | 7274.9 | 164 / 23
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:30:00 | 18:30:00 | 14:30:00 |  | 14979 | 7378 | -7601 | -1.691 | 7274.9 | 1979.6 | 23 / 103
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 18:45:00 | 18:45:00 | 14:45:00 |  | 7489.5 | 2831 | -4658.5 | -1.0364 | 1585.2 | 1409.6 | 258 / 39
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 19:00:00 | 19:00:00 | 15:00:00 |  | 2831 | 13441 | 10610 | 2.3604 | 1409.6 | 2119.7 | 39 / 123
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 19:10:00 | 19:10:00 | 15:10:00 |  | 13405 | 14473 | 1068 | 0.2376 | 1412.2 | 6447.1 | 198 / 10
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 19:15:00 | 19:15:00 | 15:15:00 |  | 14473 | 13652.5 | -820.5 | -0.1825 | 6447.1 | 7229 | 10 / 14
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 19:20:00 | 19:20:00 | 15:20:00 |  | 13652.5 | 2300.5 | -11352 | -2.5255 | 7229 | 1300 | 14 / 10
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | 2300.5 | 12839 | 10538.5 | 2.3445 | 1300 | 5940.9 | 10 / 27
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 21:10:00 | 21:10:00 | 17:10:00 |  | 12839 | 13108 | 269 | 0.0598 | 5940.9 | 7229.7 | 27 / 29
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 21:15:00 | 21:15:00 | 17:15:00 |  | 13108 | 5694 | -7414 | -1.6494 | 7229.7 | 880.7 | 29 / 86
8/22 | 75369486 | 63 Shady Lane | 2026-08-22 21:55:00 | 21:55:00 | 17:55:00 |  | 5695 | 7613 | 1918 | 0.4267 | 1434.5 | 4274.3 | 133 / 7
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 11:40:00 | 11:40:00 | 07:40:00 |  | -5835 | -6391.5 | -556.5 | -0.1238 | 1111.5 | 963.5 | 50 / 90
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 11:45:00 | 11:45:00 | 07:45:00 |  | -6391.5 | -4777 | 1614.5 | 0.3592 | 963.5 | 863.9 | 90 / 129
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 11:50:00 | 11:50:00 | 07:50:00 |  | -4777 | -80 | 4697 | 1.0449 | 863.9 | 1478.8 | 129 / 7
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 12:15:00 | 12:15:00 | 08:15:00 |  | -80 | -5138 | -5058 | -1.1253 | 1478.8 | 3937.7 | 7 / 188
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 12:30:00 | 12:30:00 | 08:30:00 |  | -4735 | -11492 | -6757 | -1.5032 | 1848.4 | 5194.9 | 193 / 61
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 12:35:00 | 12:35:00 | 08:35:00 |  | -11492 | -5333 | 6159 | 1.3702 | 5194.9 | 1634.8 | 61 / 233
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | -4909.5 | -8673.5 | -3764 | -0.8374 | 830.8 | 2408.6 | 236 / 48
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 13:00:00 | 13:00:00 | 09:00:00 |  | -8673.5 | -4645 | 4028.5 | 0.8962 | 2408.6 | 972.5 | 48 / 136
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 13:20:00 | 13:20:00 | 09:20:00 |  | -4645 | -5135 | -490 | -0.109 | 972.5 | 688 | 136 / 57
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 13:30:00 | 13:30:00 | 09:30:00 |  | -5109.5 | -4618 | 491.5 | 0.1093 | 1477.6 | 2063.5 | 22 / 8
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 13:35:00 | 13:35:00 | 09:35:00 |  | -4618 | -8759 | -4141 | -0.9212 | 2063.5 | 2130.7 | 8 / 94
8/22 | 77041962 | 40 Maple Lane APT #1 | 2026-08-22 13:40:00 | 13:40:00 | 09:40:00 |  | -8759 | -3690 | 5069 | 1.1277 | 2130.7 | 1613.4 | 94 / 15
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 10:45:00 | 10:45:00 | 06:45:00 |  | 5344 | 7718 | 2374 | 0.5281 | 1645.4 | 1286.6 | 41 / 189
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 17:45:00 | 17:45:00 | 13:45:00 |  | 7513 | 35 | -7478 | -1.6636 | 2606.2 | 2445.8 | 14 / 7
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 18:55:00 | 18:55:00 | 14:55:00 |  | 35 | 5884 | 5849 | 1.3012 | 2445.8 | 254.3 | 7 / 75
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 19:05:00 | 19:05:00 | 15:05:00 |  | 5933 | 3982 | -1951 | -0.434 | 1707.8 | 996.1 | 126 / 115
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 21:30:00 | 21:30:00 | 17:30:00 |  | 3982 | 12004.5 | 8022.5 | 1.7848 | 996.1 | 4943.1 | 115 / 40
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 21:40:00 | 21:40:00 | 17:40:00 |  | 11903 | 4721.5 | -7181.5 | -1.5977 | 4865.4 | 4183.7 | 13 / 42
8/22 | 79455422 | 76 Shady Lane | 2026-08-22 21:55:00 | 21:55:00 | 17:55:00 |  | 4721.5 | 5263.5 | 542 | 0.1206 | 4183.7 | 2653.2 | 42 / 12
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 11:00:00 | 11:00:00 | 07:00:00 |  | -5910 | -6325 | -415 | -0.0923 | 2036.4 | 1899.2 | 14 / 55
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 11:05:00 | 11:05:00 | 07:05:00 |  | -6325 | -6933.5 | -608.5 | -0.1354 | 1899.2 | 1671.6 | 55 / 64
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 11:30:00 | 11:30:00 | 07:30:00 |  | -6933.5 | -5960 | 973.5 | 0.2166 | 1671.6 | 1896.4 | 64 / 74
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 14:55:00 | 14:55:00 | 10:55:00 | YES | -5960 | -49 | 5911 | 1.315 | 1896.4 | 1445.1 | 74 / 9
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 16:40:00 | 16:40:00 | 12:40:00 | YES | -49 | -3132.5 | -3083.5 | -0.686 | 1445.1 | 1167.7 | 9 / 26
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | -3133.5 | -2419 | 714.5 | 0.159 | 810.7 | 1344.1 | 40 / 11
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 18:45:00 | 18:45:00 | 14:45:00 |  | -2419 | -7363 | -4944 | -1.0999 | 1344.1 | 1603.7 | 11 / 47
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 18:50:00 | 18:50:00 | 14:50:00 |  | -7363 | -6180.5 | 1182.5 | 0.2631 | 1603.7 | 3172.3 | 47 / 26
8/22 | 79461768 | 21 Maple Lane | 2026-08-22 19:40:00 | 19:40:00 | 15:40:00 |  | -6180.5 | -6738 | -557.5 | -0.124 | 3172.3 | 1897.7 | 26 / 50
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 10:15:00 | 10:15:00 | 06:15:00 |  | 5892.5 | 15237 | 9344.5 | 1.6498 | 2128.1 | 5452.9 | 24 / 17
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 10:20:00 | 10:20:00 | 06:20:00 |  | 15237 | 16847 | 1610 | 0.2843 | 5452.9 | 3255.8 | 17 / 115
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 10:25:00 | 10:25:00 | 06:25:00 |  | 16847 | 10570 | -6277 | -1.1082 | 3255.8 | 3456.5 | 115 / 190
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 13:40:00 | 13:40:00 | 09:40:00 |  | 10570 | 15002.5 | 4432.5 | 0.7826 | 3456.5 | 2211.4 | 190 / 64
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 13:45:00 | 13:45:00 | 09:45:00 |  | 15002.5 | 11877.5 | -3125 | -0.5517 | 2211.4 | 5887.3 | 64 / 90
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 18:35:00 | 18:35:00 | 14:35:00 |  | 12015.5 | 12641 | 625.5 | 0.1104 | 3054.8 | 2338.3 | 132 / 113
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 18:40:00 | 18:40:00 | 14:40:00 |  | 12641 | 13675 | 1034 | 0.1826 | 2338.3 | 2793.4 | 113 / 114
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 20:30:00 | 20:30:00 | 16:30:00 |  | 13675 | 15524.5 | 1849.5 | 0.3265 | 2793.4 | 3824.1 | 114 / 138
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 20:35:00 | 20:35:00 | 16:35:00 |  | 15524.5 | 3950 | -11574.5 | -2.0435 | 3824.1 | 3424.8 | 138 / 104
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 20:40:00 | 20:40:00 | 16:40:00 |  | 3950 | 1099.5 | -2850.5 | -0.5033 | 3424.8 | 1603.6 | 104 / 52
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 20:45:00 | 20:45:00 | 16:45:00 |  | 1099.5 | 5645 | 4545.5 | 0.8025 | 1603.6 | 2284.9 | 52 / 63
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 20:55:00 | 20:55:00 | 16:55:00 |  | 5645 | 797.5 | -4847.5 | -0.8558 | 2284.9 | 1766.2 | 63 / 14
8/22 | 79466304 | 5027 Spruce Lane | 2026-08-22 21:00:00 | 21:00:00 | 17:00:00 |  | 797.5 | 5830 | 5032.5 | 0.8885 | 1766.2 | 2320 | 14 / 37
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 12:15:00 | 12:15:00 | 08:15:00 |  | 9288 | 7658 | -1630 | -0.3626 | 2988 | 1698.6 | 39 / 36
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 12:25:00 | 12:25:00 | 08:25:00 |  | 7446 | 5930 | -1516 | -0.3373 | 3036.3 | 3957.4 | 94 / 75
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 12:45:00 | 12:45:00 | 08:45:00 |  | 5930 | 3938 | -1992 | -0.4432 | 3957.4 | 2048 | 75 / 12
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 12:50:00 | 12:50:00 | 08:50:00 |  | 3938 | 6060 | 2122 | 0.4721 | 2048 | 3250 | 12 / 35
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 12:55:00 | 12:55:00 | 08:55:00 |  | 6060 | 4105.5 | -1954.5 | -0.4348 | 3250 | 3902.4 | 35 / 96
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 13:00:00 | 13:00:00 | 09:00:00 |  | 4105.5 | 10872 | 6766.5 | 1.5053 | 3902.4 | 3558.3 | 96 / 20
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 13:35:00 | 13:35:00 | 09:35:00 |  | 10872 | 7175 | -3697 | -0.8225 | 3558.3 | 2272.8 | 20 / 155
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | 7175 | 714 | -6461 | -1.4374 | 2272.8 | 3036.6 | 155 / 7
8/22 | 79466379 | 106 Shady Lane | 2026-08-22 18:25:00 | 18:25:00 | 14:25:00 |  | 714 | 10251.5 | 9537.5 | 2.1218 | 3036.6 | 2989.2 | 7 / 30
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 11:05:00 | 11:05:00 | 07:05:00 |  | 7867 | 9560 | 1693 | 0.3766 | 1763.9 | 3081.7 | 63 / 19
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 13:40:00 | 13:40:00 | 09:40:00 |  | 9560 | 4844.5 | -4715.5 | -1.0491 | 3081.7 | 2474.6 | 19 / 12
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 14:30:00 | 14:30:00 | 10:30:00 | YES | 4844.5 | 6971 | 2126.5 | 0.4731 | 2474.6 | 2719.4 | 12 / 83
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 17:50:00 | 17:50:00 | 13:50:00 |  | 6971 | 6423 | -548 | -0.1219 | 2719.4 | 1570 | 83 / 165
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 17:55:00 | 17:55:00 | 13:55:00 |  | 6423 | 5657.5 | -765.5 | -0.1703 | 1570 | 269.6 | 165 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:00:00 | 18:00:00 | 14:00:00 |  | 5657.5 | 5128 | -529.5 | -0.1178 | 269.6 | 182.2 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:05:00 | 18:05:00 | 14:05:00 |  | 5128 | 5931 | 803 | 0.1786 | 182.2 | 1170.6 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:10:00 | 18:10:00 | 14:10:00 |  | 5931 | 7388.5 | 1457.5 | 0.3242 | 1170.6 | 1140.8 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:15:00 | 18:15:00 | 14:15:00 |  | 7388.5 | 5108 | -2280.5 | -0.5073 | 1140.8 | 555.8 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:20:00 | 18:20:00 | 14:20:00 |  | 5108 | 6143.5 | 1035.5 | 0.2304 | 555.8 | 281.5 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:25:00 | 18:25:00 | 14:25:00 |  | 6143.5 | 5263.5 | -880 | -0.1958 | 281.5 | 305 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 18:55:00 | 18:55:00 | 14:55:00 |  | 5896.5 | 6152 | 255.5 | 0.0568 | 160.5 | 202.4 | 136 / 291
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:00:00 | 19:00:00 | 15:00:00 |  | 6152 | 6490.5 | 338.5 | 0.0753 | 202.4 | 904.3 | 291 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:05:00 | 19:05:00 | 15:05:00 |  | 6490.5 | 8723.5 | 2233 | 0.4968 | 904.3 | 1500.8 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:10:00 | 19:10:00 | 15:10:00 |  | 8723.5 | 8338 | -385.5 | -0.0858 | 1500.8 | 255.4 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:15:00 | 19:15:00 | 15:15:00 |  | 8338 | 8609 | 271 | 0.0603 | 255.4 | 1341.6 | 300 / 300
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:25:00 | 19:25:00 | 15:25:00 |  | 8616.5 | 9023 | 406.5 | 0.0904 | 1821.9 | 2610.1 | 300 / 121
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:35:00 | 19:35:00 | 15:35:00 |  | 9023 | 3693 | -5330 | -1.1858 | 2610.1 | 1724.4 | 121 / 11
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:45:00 | 19:45:00 | 15:45:00 |  | 3458 | 7786.5 | 4328.5 | 0.963 | 1644.5 | 1220.2 | 11 / 80
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 19:50:00 | 19:50:00 | 15:50:00 |  | 7786.5 | 8302 | 515.5 | 0.1147 | 1220.2 | 1521.5 | 80 / 237
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 20:05:00 | 20:05:00 | 16:05:00 |  | 8302 | 4950 | -3352 | -0.7457 | 1521.5 | 545.3 | 237 / 129
8/22 | 79466858 | 154 Shady Lane | 2026-08-22 20:10:00 | 20:10:00 | 16:10:00 |  | 4950 | 4246 | -704 | -0.1566 | 545.3 | 907.9 | 129 / 122

## Shutoff Test 8-27
8/27 shutoff test - before vs during (CONFIRMED window)
Water-off block 16:00-20:00 UTC (12:00-16:00 EDT) confirmed by 8 of 9 full-coverage meters reading flowRate exactly 0.000. 'Before' = 11:00-15:00 UTC. With the water off a healthy meter settles to a near-zero tofNorm baseline with small sd and stops moving entirely. 27 of 29 meters logged ZERO significant transitions during the block - only 5033 Spruce and 21 Maple kept thrashing (22 each).
Device | Apartment / Lot | Samples before | tofNorm med before | sd before | Samples during | tofNorm med DURING | sd DURING | p5 during | p95 during | Shift (during - before) | gpm equiv during | flowRate med during | % zero samples | Integrated gal (4h, water OFF) | Transitions DURING shutoff | Transitions all day | Verdict
79461768 | 21 Maple Lane | 13536 | -1921 | 1504.6 | 14398 | -1967 | 1764.6 | -4978 | 829 | -46 | -0.4376 | 0.438 | 13.6 | 112.9 | 22 | 40 | ANOMALY - noise storm, no zero baseline
75367100 | 5033 Spruce Lane | 471 | 4266 | 3229.9 | 13160 | -1786 | 1648.2 | -4443 | 827 | -6052 | -0.3973 | 0 | 91.7 | 5.7 | 22 | 45 | ANOMALY - noise storm, no zero baseline
70267966 | 40 Maple Lane APT #5 | 14059 | 844 | 1400.8 | 14398 | 906 | 100.1 | 841 | 957 | 62 | 0.2016 | 0.202 | 0.2 | 48.2 | 0 | 6 | ANOMALY - baseline parked off-zero
79466452 | 144 Shady Lane - Test | 14399 | 9 | 262.9 | 14400 | 36 | 199 | -287 | 363 | 27 | 0.008 | 0 | 93.1 | 1.3 | 0 | 0 | OK - settled to zero baseline
65828520 | 40 Maple Lane APT #4 | 0 |  |  | 13042 | -11 | 187.8 | -311 | 292 |  | -0.0024 | 0 | 92.6 | 1.2 | 0 | 0 | OK - settled to zero baseline
75366953 | 152 Shady Lane | 610 | 30 | 139.7 | 14398 | 36 | 164.4 | -197 | 270 | 6 | 0.008 | 0 | 93.8 | 1.1 | 0 | 0 | OK - settled to zero baseline
75365302 | 33 Maple Lane | 3386 | 107 | 140.3 | 14399 | 87 | 140.4 | -143 | 316 | -20 | 0.0154 | 0 | 99.2 | 0.1 | 0 | 0 | OK - settled to zero baseline
65824917 | 40 Maple Lane APT #0 | 0 |  |  | 12825 | 37 | 115.7 | -153 | 227 |  | 0.0082 | 0 | 97 | 0.4 | 0 | 0 | OK - settled to zero baseline
70268832 | 116 Shady Lane | 692 | -52.5 | 123.3 | 14400 | -57 | 91.9 | -189 | 108 | -4.5 | -0.0127 | 0 | 99 | 0.1 | 0 | 0 | OK - settled to zero baseline
75368397 | 168 Shady Lane | 308 | -4473.5 | 1106.8 | 14399 | 43 | 84.6 | -96 | 183 | 4516.5 | 0.0076 | 0 | 100 | 0 | 0 | 3 | OK - settled to zero baseline
79466304 | 5027 Spruce Lane | 1461 | 32 | 5326.8 | 14397 | 13 | 68.1 | -99 | 125 | -19 | 0.0023 | 0 | 100 | 0 | 0 | 7 | OK - settled to zero baseline
75368777 | 144 Shady Lane-Old | 14398 | 29 | 33.3 | 7144 | 73 | 56.9 | -9 | 176 | 44 | 0.0162 | 0 | 99.9 | 0 | 0 | 0 | OK - settled to zero baseline
79466858 | 154 Shady Lane | 1265 | 44 | 2164.7 | 14398 | 8 | 53.5 | -81 | 95 | -36 | 0.0018 | 0 | 100 | 0 | 0 | 4 | OK - settled to zero baseline
75363992 | 84 Shady Lane | 0 |  |  | 14398 | 29 | 52.1 | -48 | 103 |  | 0.0051 | 0 | 99.9 | 0 | 0 | 0 | OK - settled to zero baseline
75368439 | 44 Shady Lane | 3007 | 26 | 4250.2 | 14398 | -14 | 47.6 | -93 | 65 | -40 | -0.0025 | 0 | 100 | 0 | 0 | 9 | OK - settled to zero baseline
79466379 | 106 Shady Lane | 1717 | 6 | 2131.4 | 14397 | -39 | 46.2 | -117 | 36 | -45 | -0.0087 | 0 | 100 | 0 | 0 | 3 | OK - settled to zero baseline
75365898 | 136 Shady Lane | 0 |  |  | 13637 | -6 | 44.3 | -79 | 66 |  | -0.0013 | 0 | 100 | 0 | 0 | 0 | OK - settled to zero baseline
75366029 | 148 Shady Lane | 3501 | 20 | 3191 | 14398 | 14 | 43.9 | -59 | 86 | -6 | 0.0031 | 0 | 100 | 0 | 0 | 5 | OK - settled to zero baseline
75365427 | 132 Shady Lane | 184 | 8551.5 | 3499 | 14399 | -44 | 42.9 | -114 | 27 | -8595.5 | -0.0078 | 0 | 100 | 0 | 0 | 4 | OK - settled to zero baseline
77041962 | 40 Maple Lane APT #1 | 2117 | -16 | 1882.8 | 9540 | -6 | 40.4 | -39 | 26 | 10 | -0.0013 | 0 | 100 | 0 | 0 | 4 | OK - settled to zero baseline
79466007 | 126 Shady Lane | 370 | -14 | 38.1 | 14400 | -21 | 38.8 | -83 | 44 | -7 | -0.0047 | 0 | 100 | 0 | 0 | 0 | OK - settled to zero baseline
77054957 | 40 Maple Lane APT #2 | 641 | 0 | 19.3 | 14398 | -1 | 37.3 | -33 | 31 | -1 | -0.0002 | 0 | 99.9 | 0 | 0 | 0 | OK - settled to zero baseline
75369486 | 63 Shady Lane | 3303 | 4 | 2536.9 | 14398 | 16 | 37 | -41 | 73 | 12 | 0.0036 | 0 | 100 | 0 | 0 | 12 | OK - settled to zero baseline
75363901 | 75 Shady Lane | 2953 | -46 | 296.8 | 14399 | -9 | 31.2 | -63 | 39 | 37 | -0.002 | 0 | 100 | 0 | 0 | 1 | OK - settled to zero baseline
65823489 | 138 | 322 | 10112.5 | 4069.5 | 14398 | -33 | 27.3 | -78 | 13 | -10145.5 | -0.0058 | 0 | 100 | 0 | 0 | 7 | OK - settled to zero baseline
75366011 | 96 Shady Lane | 2535 | 0 | 24.3 | 14398 | 10 | 22 | -26 | 46 | 10 | 0.0022 | 0 | 100 | 0 | 0 | 0 | OK - settled to zero baseline
75364586 | 103 Shady Lane | 421 | 11270 | 6901.5 | 0 | [9 empty] | 0 | 7 | insufficient data
75366938 | 29 Maple Lane | 132 | 4402 | 5905.3 | 0 | [9 empty] | 0 | 3 | insufficient data
79461115 | 15 Maple Lane | 82 | 6787 | 5186.8 | 0 | [9 empty] | 0 | 1 | insufficient data

## Shutoff Test 8-22
8/22 shutoff test - INFERRED window, low confidence
CAVEAT: on 8/22 the meters were still in event-only recording, so tofNorm exists only while the meter thought water was moving. The window (14:00-17:30 UTC) was inferred from the event ramp and is NOT reliable. The residual/bias table derived from this window has been RETRACTED. Retained here only as a record of what data exists.
Device | Apartment / Lot | Samples before | tofNorm med before | Samples during | tofNorm med during | sd during | Shift | gpm equiv | flowRate med during | Integrated gal | Note
70267966 | 40 Maple Lane APT #5 | 2759 | 5620 | 1845 | 5432 | 2658.3 | -188 | 1.2085 | 1.208 | 39.4 | event-mode only - not a zero-flow reference
75363992 | 84 Shady Lane | 538 | 7217.5 | 356 | 6446.5 | 2658.3 | -771 | 1.1382 | 1.138 | 5.2 | event-mode only - not a zero-flow reference
75363901 | 75 Shady Lane | 176 | -4783 | 295 | -4413 | 1483.7 | 370 | -0.9818 | 0.982 | 4.3 | event-mode only - not a zero-flow reference
75366029 | 148 Shady Lane | 1392 | -4959.5 | 244 | -2364.5 | 5144.3 | 2595 | -0.526 | 0.526 | 4.2 | event-mode only - not a zero-flow reference
79466858 | 154 Shady Lane | 94 | 7731.5 | 83 | 6971 | 2719.4 | -760.5 | 1.5508 | 1.551 | 1.6 | event-mode only - not a zero-flow reference
65828520 | 40 Maple Lane APT #4 | 96 | 9603 | 81 | 6079 | 3483.9 | -3524 | 1.3524 | 1.352 | 2 | event-mode only - not a zero-flow reference
75362887 | 66 Shady Lane | 816 | -3163.5 | 35 | -3953 | 1794.5 | -789.5 | -0.8794 | 0.879 | 0.4 | event-mode only - not a zero-flow reference
79461768 | 21 Maple Lane | 207 | -6325 | 35 | -2940 | 1683.6 | 3385 | -0.6541 | 0.654 | 0.3 | event-mode only - not a zero-flow reference
75366938 | 29 Maple Lane | 317 | 2573 | 34 | 3764.5 | 1929 | 1191.5 | 0.8375 | 0.837 | 0.4 | event-mode only - not a zero-flow reference
75364586 | 103 Shady Lane | 204 | 4037 | 27 | 3945 | 1443.3 | -92 | 0.8776 | 0.878 | 0.3 | event-mode only - not a zero-flow reference
75368397 | 168 Shady Lane | 1579 | -4483 | 14 | -4100 | 1746.8 | 383 | -0.7239 | 0.724 | 0.1 | event-mode only - not a zero-flow reference
75369486 | 63 Shady Lane | 0 |  | 6 | 4512.5 | 2348.6 |  | 1.0039 | 1.004 | 0.1 | event-mode only - not a zero-flow reference
65823489 | 138 | 272 | 10821.5 | 0 | [6 empty] | event-mode only - not a zero-flow reference
70268832 | 116 Shady Lane | 49 | -3223 | 0 | [6 empty] | event-mode only - not a zero-flow reference
75364883 | 5019 Spruce Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
75365302 | 33 Maple Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
75365427 | 132 Shady Lane | 219 | 9357 | 0 | [6 empty] | event-mode only - not a zero-flow reference
75365898 | 136 Shady Lane | 600 | -5255.5 | 0 | [6 empty] | event-mode only - not a zero-flow reference
75366011 | 96 Shady Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
75366953 | 152 Shady Lane | 57 | 10331 | 0 | [6 empty] | event-mode only - not a zero-flow reference
75367100 | 5033 Spruce Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
75368439 | 44 Shady Lane | 200 | 8137.5 | 0 | [6 empty] | event-mode only - not a zero-flow reference
75368777 | 144 Shady Lane-Old | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
75369098 | 5013 Spruce Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
77041962 | 40 Maple Lane APT #1 | 2142 | -5018 | 0 | [6 empty] | event-mode only - not a zero-flow reference
79455422 | 76 Shady Lane | 244 | 7639 | 0 | [6 empty] | event-mode only - not a zero-flow reference
79466007 | 126 Shady Lane | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference
79466304 | 5027 Spruce Lane | 500 | 12091.5 | 0 | [6 empty] | event-mode only - not a zero-flow reference
79466379 | 106 Shady Lane | 562 | 7309 | 0 | [6 empty] | event-mode only - not a zero-flow reference
79466452 | 144 Shady Lane - Test | 0 |  | 0 | [6 empty] | event-mode only - not a zero-flow reference

## Hourly Grid 8-27
8/27 hourly tofNorm / flow grid (continuous samples)
Per device per hour. Rows inside the confirmed water-off block are flagged. Read the sd column: healthy meters hold sd under about 50 with the water off.
Device | Apartment / Lot | Hour (UTC) | Hour (EDT) | In shutoff? | Samples | tofNorm median | tofNorm sd | Quiet samples | Quiet tofNorm median | flowRate median | Integrated gal
65823489 | 138 | 11:00 | 07:00 |  | 204 | 10518.5 | 4361.5 | 16 | 0.5 | 1.857 | 4.97
65823489 | 138 | 12:00 | 08:00 |  | 61 | 11702 | 4239.1 | 6 | 8.5 | 2.066 | 1.6
65823489 | 138 | 14:00 | 10:00 |  | 57 | 9510 | 2393.4 | 2 | -15.5 | 1.679 | 1.49
65823489 | 138 | 15:00 | 11:00 |  | 3403 | -17 | 1163.6 | 3318 | -18 | 0 | 1.71
65823489 | 138 | 16:00 | 12:00 | YES | 3598 | -33 | 27.2 | 3598 | -33 | 0 | 0
65823489 | 138 | 17:00 | 13:00 | YES | 3600 | -25 | 29.3 | 3600 | -25 | 0 | 0
65823489 | 138 | 18:00 | 14:00 | YES | 3600 | -31 | 25.9 | 3600 | -31 | 0 | 0
65823489 | 138 | 19:00 | 15:00 | YES | 3600 | -42 | 23.9 | 3600 | -42 | 0 | 0
65824917 | 40 Maple Lane APT #0 | 16:00 | 12:00 | YES | 2025 | 30 | 112.1 | 1971 | 26 | 0 | 0.06
65824917 | 40 Maple Lane APT #0 | 17:00 | 13:00 | YES | 3600 | 36 | 113.2 | 3506 | 32 | 0 | 0.11
65824917 | 40 Maple Lane APT #0 | 18:00 | 14:00 | YES | 3600 | 43 | 116 | 3478 | 36 | 0 | 0.13
65824917 | 40 Maple Lane APT #0 | 19:00 | 15:00 | YES | 3600 | 37 | 119.5 | 3487 | 33 | 0 | 0.13
65828520 | 40 Maple Lane APT #4 | 16:00 | 12:00 | YES | 2243 | -12 | 178.9 | 2076 | -28.5 | 0 | 0.21
65828520 | 40 Maple Lane APT #4 | 17:00 | 13:00 | YES | 3599 | 1 | 202.9 | 3290 | -15 | 0 | 0.39
65828520 | 40 Maple Lane APT #4 | 18:00 | 14:00 | YES | 3600 | -21 | 176.9 | 3386 | -35 | 0 | 0.26
65828520 | 40 Maple Lane APT #4 | 19:00 | 15:00 | YES | 3600 | -17.5 | 187.6 | 3321 | -34 | 0 | 0.36
70267966 | 40 Maple Lane APT #5 | 11:00 | 07:00 |  | 3334 | 820 | 2303.3 | 0 |  | 0.182 | 19.43
70267966 | 40 Maple Lane APT #5 | 12:00 | 08:00 |  | 3525 | 832 | 1520 | 0 |  | 0.185 | 16.61
70267966 | 40 Maple Lane APT #5 | 13:00 | 09:00 |  | 3600 | 859 | 323.6 | 0 |  | 0.191 | 11.77
70267966 | 40 Maple Lane APT #5 | 14:00 | 10:00 |  | 3600 | 855 | 226.8 | 0 |  | 0.19 | 11.56
70267966 | 40 Maple Lane APT #5 | 15:00 | 11:00 |  | 3262 | 861 | 2272.3 | 0 |  | 0.192 | 26.13
70267966 | 40 Maple Lane APT #5 | 16:00 | 12:00 | YES | 3598 | 869 | 154.2 | 0 |  | 0.193 | 11.68
70267966 | 40 Maple Lane APT #5 | 17:00 | 13:00 | YES | 3600 | 909 | 104.1 | 22 | -186 | 0.202 | 12.05
70267966 | 40 Maple Lane APT #5 | 18:00 | 14:00 | YES | 3600 | 912 | 31.6 | 0 |  | 0.203 | 12.16
70267966 | 40 Maple Lane APT #5 | 19:00 | 15:00 | YES | 3600 | 924 | 57.9 | 5 | 104 | 0.206 | 12.27
70268832 | 116 Shady Lane | 14:00 | 10:00 |  | 692 | -52.5 | 123.3 | 665 | -45 | 0 | 0.03
70268832 | 116 Shady Lane | 15:00 | 11:00 |  | 3598 | -38 | 115.7 | 3513 | -34 | 0 | 0.09
70268832 | 116 Shady Lane | 16:00 | 12:00 | YES | 3600 | -52 | 101.8 | 3539 | -50 | 0 | 0.07
70268832 | 116 Shady Lane | 17:00 | 13:00 | YES | 3600 | -51 | 98.1 | 3563 | -50 | 0 | 0.04
70268832 | 116 Shady Lane | 18:00 | 14:00 | YES | 3600 | -67 | 84.8 | 3575 | -66 | 0 | 0.03
70268832 | 116 Shady Lane | 19:00 | 15:00 | YES | 3600 | -56.5 | 80.6 | 3583 | -56 | 0 | 0.02
75363901 | 75 Shady Lane | 12:00 | 08:00 |  | 14 | -5223 | 2460.5 | 3 | 11 | 1.162 | 0.19
75363901 | 75 Shady Lane | 14:00 | 10:00 |  | 2939 | -46 | 27.3 | 2939 | -46 | 0 | 0
75363901 | 75 Shady Lane | 15:00 | 11:00 |  | 3600 | -46 | 27.3 | 3600 | -46 | 0 | 0
75363901 | 75 Shady Lane | 16:00 | 12:00 | YES | 3599 | -23 | 35.5 | 3599 | -23 | 0 | 0
75363901 | 75 Shady Lane | 17:00 | 13:00 | YES | 3600 | -5 | 28.4 | 3600 | -5 | 0 | 0
75363901 | 75 Shady Lane | 18:00 | 14:00 | YES | 3600 | -6 | 28 | 3600 | -6 | 0 | 0
75363901 | 75 Shady Lane | 19:00 | 15:00 | YES | 3600 | -7 | 28.4 | 3600 | -7 | 0 | 0
75363992 | 84 Shady Lane | 15:00 | 11:00 |  | 1231 | 34 | 46 | 1231 | 34 | 0 | 0
75363992 | 84 Shady Lane | 16:00 | 12:00 | YES | 3598 | 34 | 42.9 | 3598 | 34 | 0 | 0
75363992 | 84 Shady Lane | 17:00 | 13:00 | YES | 3600 | 31 | 46.2 | 3594 | 31 | 0 | 0.01
75363992 | 84 Shady Lane | 18:00 | 14:00 | YES | 3600 | 39 | 52 | 3587 | 39 | 0 | 0.01
75363992 | 84 Shady Lane | 19:00 | 15:00 | YES | 3600 | 9 | 60 | 3600 | 9 | 0 | 0
75364586 | 103 Shady Lane | 11:00 | 07:00 |  | 37 | 3852 | 2147.6 | 8 | -135.5 | 0.857 | 0.43
75364586 | 103 Shady Lane | 12:00 | 08:00 |  | 132 | 4141.5 | 1900.2 | 26 | -12.5 | 0.921 | 1.64
75364586 | 103 Shady Lane | 13:00 | 09:00 |  | 252 | 14418.5 | 4998.1 | 9 | 23 | 3.207 | 13.71
75365302 | 33 Maple Lane | 14:00 | 10:00 |  | 3386 | 107 | 140.3 | 3370 | 107 | 0 | 0.01
75365302 | 33 Maple Lane | 15:00 | 11:00 |  | 3598 | 114.5 | 138.5 | 3588 | 115 | 0 | 0.01
75365302 | 33 Maple Lane | 16:00 | 12:00 | YES | 3599 | 128 | 138.2 | 3590 | 128 | 0 | 0.01
75365302 | 33 Maple Lane | 17:00 | 13:00 | YES | 3600 | 84 | 137.3 | 3569 | 85 | 0 | 0.03
75365302 | 33 Maple Lane | 18:00 | 14:00 | YES | 3600 | 68 | 138.9 | 3558 | 70.5 | 0 | 0.04
75365302 | 33 Maple Lane | 19:00 | 15:00 | YES | 3600 | 64 | 137.4 | 3571 | 65 | 0 | 0.03
75365427 | 132 Shady Lane | 12:00 | 08:00 |  | 104 | 10462 | 4100.3 | 10 | -51 | 1.847 | 2.23
75365427 | 132 Shady Lane | 13:00 | 09:00 |  | 80 | 8526.5 | 2505.6 | 2 | 129 | 1.505 | 1.76
75365427 | 132 Shady Lane | 15:00 | 11:00 |  | 2868 | -44.5 | 39.2 | 2868 | -44.5 | 0 | 0
75365427 | 132 Shady Lane | 16:00 | 12:00 | YES | 3600 | -49 | 40 | 3600 | -49 | 0 | 0
75365427 | 132 Shady Lane | 17:00 | 13:00 | YES | 3599 | -46 | 41.5 | 3599 | -46 | 0 | 0
75365427 | 132 Shady Lane | 18:00 | 14:00 | YES | 3600 | -45 | 43.1 | 3600 | -45 | 0 | 0
75365427 | 132 Shady Lane | 19:00 | 15:00 | YES | 3600 | -34 | 45.2 | 3600 | -34 | 0 | 0
75365898 | 136 Shady Lane | 16:00 | 12:00 | YES | 2837 | -11 | 43.4 | 2837 | -11 | 0 | 0
75365898 | 136 Shady Lane | 17:00 | 13:00 | YES | 3600 | -5 | 44.4 | 3600 | -5 | 0 | 0
75365898 | 136 Shady Lane | 18:00 | 14:00 | YES | 3600 | -3 | 43.9 | 3600 | -3 | 0 | 0
75365898 | 136 Shady Lane | 19:00 | 15:00 | YES | 3600 | -6 | 44.9 | 3600 | -6 | 0 | 0
75366011 | 96 Shady Lane | 14:00 | 10:00 |  | 2535 | 0 | 24.3 | 2535 | 0 | 0 | 0
75366011 | 96 Shady Lane | 15:00 | 11:00 |  | 3600 | 6 | 21.5 | 3600 | 6 | 0 | 0
75366011 | 96 Shady Lane | 16:00 | 12:00 | YES | 3600 | 5 | 20.9 | 3600 | 5 | 0 | 0
75366011 | 96 Shady Lane | 17:00 | 13:00 | YES | 3598 | 10 | 21.1 | 3598 | 10 | 0 | 0
75366011 | 96 Shady Lane | 18:00 | 14:00 | YES | 3600 | 10 | 21.8 | 3600 | 10 | 0 | 0
75366011 | 96 Shady Lane | 19:00 | 15:00 | YES | 3600 | 17 | 22.3 | 3600 | 17 | 0 | 0
75366029 | 148 Shady Lane | 11:00 | 07:00 |  | 360 | -2720.5 | 6977.8 | 16 | -10 | 0.605 | 9.96
75366029 | 148 Shady Lane | 14:00 | 10:00 |  | 3141 | 26 | 39.5 | 3140 | 26 | 0 | 0
75366029 | 148 Shady Lane | 15:00 | 11:00 |  | 3600 | 32 | 36.8 | 3600 | 32 | 0 | 0
75366029 | 148 Shady Lane | 16:00 | 12:00 | YES | 3598 | 33 | 37.6 | 3598 | 33 | 0 | 0
75366029 | 148 Shady Lane | 17:00 | 13:00 | YES | 3600 | 38 | 38.4 | 3600 | 38 | 0 | 0
75366029 | 148 Shady Lane | 18:00 | 14:00 | YES | 3600 | -10 | 38.4 | 3600 | -10 | 0 | 0
75366029 | 148 Shady Lane | 19:00 | 15:00 | YES | 3600 | -5 | 38 | 3600 | -5 | 0 | 0
75366938 | 29 Maple Lane | 11:00 | 07:00 |  | 132 | 4402 | 5905.3 | 20 | 40.5 | 0.979 | 3.77
75366953 | 152 Shady Lane | 14:00 | 10:00 |  | 610 | 30 | 139.7 | 579 | 25 | 0 | 0.03
75366953 | 152 Shady Lane | 15:00 | 11:00 |  | 3600 | 49 | 151.5 | 3317 | 35 | 0 | 0.35
75366953 | 152 Shady Lane | 16:00 | 12:00 | YES | 3598 | 28 | 141.3 | 3400 | 20 | 0 | 0.23
75366953 | 152 Shady Lane | 17:00 | 13:00 | YES | 3600 | 28 | 185.6 | 3378 | 18 | 0 | 0.26
75366953 | 152 Shady Lane | 18:00 | 14:00 | YES | 3600 | 47 | 187 | 3330 | 36 | 0 | 0.34
75366953 | 152 Shady Lane | 19:00 | 15:00 | YES | 3600 | 39 | 135.7 | 3397 | 30 | 0 | 0.24
75367100 | 5033 Spruce Lane | 11:00 | 07:00 |  | 132 | 5467 | 3232.3 | 25 | -1361 | 1.216 | 2.25
75367100 | 5033 Spruce Lane | 12:00 | 08:00 |  | 59 | -159 | 2552.4 | 35 | -1720 | 0 | 0.25
75367100 | 5033 Spruce Lane | 13:00 | 09:00 |  | 100 | 4914.5 | 2806.5 | 18 | -849.5 | 1.093 | 1.59
75367100 | 5033 Spruce Lane | 14:00 | 10:00 |  | 180 | 3917.5 | 2908.7 | 37 | -1638 | 0.871 | 2.2
75367100 | 5033 Spruce Lane | 15:00 | 11:00 |  | 175 | -335 | 2550.5 | 93 | -1920 | 0 | 0.75
75367100 | 5033 Spruce Lane | 16:00 | 12:00 | YES | 2360 | -1831 | 1781.9 | 2154 | -1988 | 0 | 1.15
75367100 | 5033 Spruce Lane | 17:00 | 13:00 | YES | 3600 | -1951.5 | 1506.4 | 3380 | -2053.5 | 0 | 0.93
75367100 | 5033 Spruce Lane | 18:00 | 14:00 | YES | 3600 | -1792.5 | 1739.2 | 3275 | -1959 | 0 | 1.71
75367100 | 5033 Spruce Lane | 19:00 | 15:00 | YES | 3600 | -1607 | 1574.2 | 3261 | -1759 | 0 | 1.94
75368397 | 168 Shady Lane | 11:00 | 07:00 |  | 172 | -4877 | 1099.8 | 4 | 81.5 | 0.861 | 2.3
75368397 | 168 Shady Lane | 13:00 | 09:00 |  | 130 | -4415.5 | 773.6 | 3 | 12 | 0.78 | 1.62
75368397 | 168 Shady Lane | 14:00 | 10:00 |  | 6 | -657 | 734.6 | 2 | 52.5 | 0.116 | 0.01
75368397 | 168 Shady Lane | 15:00 | 11:00 |  | 2144 | 25 | 84.8 | 2143 | 25 | 0 | 0
75368397 | 168 Shady Lane | 16:00 | 12:00 | YES | 3600 | 52 | 78.1 | 3599 | 52 | 0 | 0
75368397 | 168 Shady Lane | 17:00 | 13:00 | YES | 3599 | 60 | 81.3 | 3598 | 60 | 0 | 0
75368397 | 168 Shady Lane | 18:00 | 14:00 | YES | 3600 | 48 | 87.7 | 3598 | 48 | 0 | 0
75368397 | 168 Shady Lane | 19:00 | 15:00 | YES | 3600 | 11 | 83.3 | 3599 | 11 | 0 | 0
75368439 | 44 Shady Lane | 11:00 | 07:00 |  | 174 | 16869 | 5873.6 | 5 | 30 | 2.978 | 6.21
75368439 | 44 Shady Lane | 12:00 | 08:00 |  | 292 | 5796.5 | 4294.5 | 8 | -41.5 | 1.023 | 6.66
75368439 | 44 Shady Lane | 13:00 | 09:00 |  | 108 | 7867 | 2052.9 | 7 | 39 | 1.389 | 2.31
75368439 | 44 Shady Lane | 14:00 | 10:00 |  | 2433 | 8 | 1961.9 | 2028 | -2 | 0 | 6.18
75368439 | 44 Shady Lane | 15:00 | 11:00 |  | 3600 | 7 | 1494.7 | 3113 | -1 | 0 | 6.18
75368439 | 44 Shady Lane | 16:00 | 12:00 | YES | 3598 | -16 | 45.2 | 3598 | -16 | 0 | 0
75368439 | 44 Shady Lane | 17:00 | 13:00 | YES | 3600 | -30 | 47.4 | 3600 | -30 | 0 | 0
75368439 | 44 Shady Lane | 18:00 | 14:00 | YES | 3600 | -9 | 46.8 | 3600 | -9 | 0 | 0
75368439 | 44 Shady Lane | 19:00 | 15:00 | YES | 3600 | 0 | 45.4 | 3600 | 0 | 0 | 0
75368777 | 144 Shady Lane-Old | 11:00 | 07:00 |  | 3600 | 28 | 31.7 | 3599 | 28 | 0 | 0
75368777 | 144 Shady Lane-Old | 12:00 | 08:00 |  | 3600 | 33 | 30.6 | 3600 | 33 | 0 | 0
75368777 | 144 Shady Lane-Old | 13:00 | 09:00 |  | 3600 | 31 | 30.7 | 3600 | 31 | 0 | 0
75368777 | 144 Shady Lane-Old | 14:00 | 10:00 |  | 3598 | 20 | 38.2 | 3598 | 20 | 0 | 0
75368777 | 144 Shady Lane-Old | 15:00 | 11:00 |  | 2830 | 19 | 102.6 | 2805 | 18 | 0 | 0.03
75368777 | 144 Shady Lane-Old | 16:00 | 12:00 | YES | 3600 | 114 | 50.1 | 3594 | 113 | 0 | 0.01
75368777 | 144 Shady Lane-Old | 17:00 | 13:00 | YES | 3544 | 44 | 38 | 3544 | 44 | 0 | 0
75369486 | 63 Shady Lane | 11:00 | 07:00 |  | 85 | 2850 | 4096.7 | 11 | 7 | 0.634 | 1.63
75369486 | 63 Shady Lane | 12:00 | 08:00 |  | 140 | 1693 | 4178.5 | 15 | 10 | 0.377 | 2.04
75369486 | 63 Shady Lane | 13:00 | 09:00 |  | 133 | 7435 | 4242 | 21 | 2 | 1.654 | 3.35
75369486 | 63 Shady Lane | 14:00 | 10:00 |  | 2945 | 0 | 1462.9 | 2827 | -2 | 0 | 2.69
75369486 | 63 Shady Lane | 15:00 | 11:00 |  | 3600 | 1 | 532.1 | 3461 | -1 | 0 | 1.27
75369486 | 63 Shady Lane | 16:00 | 12:00 | YES | 3598 | 8 | 31.3 | 3598 | 8 | 0 | 0
75369486 | 63 Shady Lane | 17:00 | 13:00 | YES | 3600 | 22 | 31.2 | 3600 | 22 | 0 | 0
75369486 | 63 Shady Lane | 18:00 | 14:00 | YES | 3600 | 27 | 40.6 | 3593 | 27 | 0 | 0.01
75369486 | 63 Shady Lane | 19:00 | 15:00 | YES | 3600 | 4.5 | 38 | 3600 | 4.5 | 0 | 0
77041962 | 40 Maple Lane APT #1 | 12:00 | 08:00 |  | 42 | -10032.5 | 3131.9 | 3 | 12 | 2.232 | 1.39
77041962 | 40 Maple Lane APT #1 | 13:00 | 09:00 |  | 102 | -3869.5 | 3952.1 | 20 | -17.5 | 0.861 | 1.9
77041962 | 40 Maple Lane APT #1 | 14:00 | 10:00 |  | 1973 | -15 | 20.4 | 1973 | -15 | 0 | 0
77041962 | 40 Maple Lane APT #1 | 15:00 | 11:00 |  | 3600 | -12 | 19.1 | 3600 | -12 | 0 | 0
77041962 | 40 Maple Lane APT #1 | 16:00 | 12:00 | YES | 3598 | -9 | 19.2 | 3598 | -9 | 0 | 0
77041962 | 40 Maple Lane APT #1 | 17:00 | 13:00 | YES | 3600 | -4 | 60.7 | 3600 | -4 | 0 | 0
77041962 | 40 Maple Lane APT #1 | 18:00 | 14:00 | YES | 2342 | -5 | 19.5 | 2342 | -5 | 0 | 0
77054957 | 40 Maple Lane APT #2 | 14:00 | 10:00 |  | 641 | 0 | 19.3 | 641 | 0 | 0 | 0
77054957 | 40 Maple Lane APT #2 | 15:00 | 11:00 |  | 3600 | -7 | 20.1 | 3600 | -7 | 0 | 0
77054957 | 40 Maple Lane APT #2 | 16:00 | 12:00 | YES | 3598 | -5 | 19.3 | 3598 | -5 | 0 | 0
77054957 | 40 Maple Lane APT #2 | 17:00 | 13:00 | YES | 3600 | 0 | 63.3 | 3595 | 0 | 0 | 0.03
77054957 | 40 Maple Lane APT #2 | 18:00 | 14:00 | YES | 3600 | 0 | 20.3 | 3600 | 0 | 0 | 0
77054957 | 40 Maple Lane APT #2 | 19:00 | 15:00 | YES | 3600 | 0 | 27.4 | 3596 | 0 | 0 | 0.01
79461115 | 15 Maple Lane | 12:00 | 08:00 |  | 33 | 15839 | 4569.7 | 3 | 59 | 2.796 | 1.4
79461115 | 15 Maple Lane | 13:00 | 09:00 |  | 30 | 6746.5 | 1619 | 1 | 50 | 1.191 | 0.56
79461115 | 15 Maple Lane | 14:00 | 10:00 |  | 19 | 6664 | 2133.9 | 2 | -32.5 | 1.177 | 0.32
79461768 | 21 Maple Lane | 11:00 | 07:00 |  | 3513 | -1741 | 1465.6 | 397 | 441 | 0.387 | 24.37
79461768 | 21 Maple Lane | 12:00 | 08:00 |  | 3556 | -2025 | 1477.4 | 304 | 390.5 | 0.45 | 28.15
79461768 | 21 Maple Lane | 13:00 | 09:00 |  | 3523 | -1867 | 1488.8 | 355 | 497 | 0.415 | 26.36
79461768 | 21 Maple Lane | 14:00 | 10:00 |  | 2944 | -2046.5 | 1577.2 | 291 | 471 | 0.455 | 23.65
79461768 | 21 Maple Lane | 15:00 | 11:00 |  | 3600 | -2165 | 1708.1 | 432 | 460 | 0.482 | 30.07
79461768 | 21 Maple Lane | 16:00 | 12:00 | YES | 3598 | -2087.5 | 1806 | 470 | 566.5 | 0.464 | 29.7
79461768 | 21 Maple Lane | 17:00 | 13:00 | YES | 3600 | -1976.5 | 1800.7 | 477 | 588 | 0.44 | 28.72
79461768 | 21 Maple Lane | 18:00 | 14:00 | YES | 3600 | -1946.5 | 1711.3 | 500 | 523 | 0.433 | 27.51
79461768 | 21 Maple Lane | 19:00 | 15:00 | YES | 3600 | -1856 | 1730.5 | 505 | 614 | 0.413 | 26.95
79466007 | 126 Shady Lane | 14:00 | 10:00 |  | 370 | -14 | 38.1 | 370 | -14 | 0 | 0
79466007 | 126 Shady Lane | 15:00 | 11:00 |  | 3600 | -7 | 34.8 | 3600 | -7 | 0 | 0
79466007 | 126 Shady Lane | 16:00 | 12:00 | YES | 3600 | -25 | 34.8 | 3600 | -25 | 0 | 0
79466007 | 126 Shady Lane | 17:00 | 13:00 | YES | 3600 | -33 | 34.8 | 3600 | -33 | 0 | 0
79466007 | 126 Shady Lane | 18:00 | 14:00 | YES | 3600 | -27 | 39.8 | 3600 | -27 | 0 | 0
79466007 | 126 Shady Lane | 19:00 | 15:00 | YES | 3600 | 3 | 35 | 3600 | 3 | 0 | 0
79466304 | 5027 Spruce Lane | 11:00 | 07:00 |  | 288 | 11952.5 | 3751.3 | 13 | -17 | 2.11 | 8.8
79466304 | 5027 Spruce Lane | 12:00 | 08:00 |  | 112 | 14334.5 | 2975.7 | 3 | -44 | 2.531 | 4.28
79466304 | 5027 Spruce Lane | 14:00 | 10:00 |  | 1061 | 1 | 66.2 | 1061 | 1 | 0 | 0
79466304 | 5027 Spruce Lane | 15:00 | 11:00 |  | 3600 | 18 | 1620.2 | 3431 | 14 | 0 | 3.66
79466304 | 5027 Spruce Lane | 16:00 | 12:00 | YES | 3598 | 18 | 65.8 | 3598 | 18 | 0 | 0
79466304 | 5027 Spruce Lane | 17:00 | 13:00 | YES | 3599 | 22 | 67.3 | 3599 | 22 | 0 | 0
79466304 | 5027 Spruce Lane | 18:00 | 14:00 | YES | 3600 | 12 | 68.3 | 3600 | 12 | 0 | 0
79466304 | 5027 Spruce Lane | 19:00 | 15:00 | YES | 3600 | 2 | 69.3 | 3600 | 2 | 0 | 0
79466379 | 106 Shady Lane | 11:00 | 07:00 |  | 115 | 5187 | 3387.6 | 11 | 18 | 1.154 | 2.53
79466379 | 106 Shady Lane | 12:00 | 08:00 |  | 37 | 9549 | 2845.9 | 3 | 36 | 2.124 | 1.18
79466379 | 106 Shady Lane | 14:00 | 10:00 |  | 1565 | 1 | 43.4 | 1565 | 1 | 0 | 0
79466379 | 106 Shady Lane | 15:00 | 11:00 |  | 3600 | -10 | 46.9 | 3600 | -10 | 0 | 0
79466379 | 106 Shady Lane | 16:00 | 12:00 | YES | 3597 | -30 | 45.9 | 3597 | -30 | 0 | 0
79466379 | 106 Shady Lane | 17:00 | 13:00 | YES | 3600 | -39.5 | 45.3 | 3600 | -39.5 | 0 | 0
79466379 | 106 Shady Lane | 18:00 | 14:00 | YES | 3600 | -45 | 45.8 | 3600 | -45 | 0 | 0
79466379 | 106 Shady Lane | 19:00 | 15:00 | YES | 3600 | -45 | 45.9 | 3600 | -45 | 0 | 0
79466452 | 144 Shady Lane - Test | 11:00 | 07:00 |  | 3600 | 12 | 259.3 | 3032 | 61 | 0 | 0.81
79466452 | 144 Shady Lane - Test | 12:00 | 08:00 |  | 3600 | 4.5 | 268.5 | 3010 | 55 | 0 | 0.89
79466452 | 144 Shady Lane - Test | 13:00 | 09:00 |  | 3600 | 1 | 264.5 | 2981 | 64 | 0 | 0.92
79466452 | 144 Shady Lane - Test | 14:00 | 10:00 |  | 3599 | 16 | 258.5 | 3080 | 67 | 0 | 0.74
79466452 | 144 Shady Lane - Test | 15:00 | 11:00 |  | 3389 | 21 | 261.6 | 2885 | 72 | 0 | 0.72
79466452 | 144 Shady Lane - Test | 16:00 | 12:00 | YES | 3600 | 30 | 207.4 | 3327 | 50 | 0 | 0.35
79466452 | 144 Shady Lane - Test | 17:00 | 13:00 | YES | 3600 | 29 | 198.4 | 3347 | 45 | 0 | 0.32
79466452 | 144 Shady Lane - Test | 18:00 | 14:00 | YES | 3600 | 42 | 194.2 | 3364 | 59 | 0 | 0.3
79466452 | 144 Shady Lane - Test | 19:00 | 15:00 | YES | 3600 | 41 | 195.4 | 3362 | 58 | 0 | 0.3
79466858 | 154 Shady Lane | 12:00 | 08:00 |  | 72 | 6661 | 1551.3 | 3 | -1 | 1.482 | 1.66
79466858 | 154 Shady Lane | 13:00 | 09:00 |  | 120 | 6556.5 | 2319.4 | 6 | 124.5 | 1.459 | 2.33
79466858 | 154 Shady Lane | 14:00 | 10:00 |  | 1073 | 34 | 46.7 | 1073 | 34 | 0 | 0
79466858 | 154 Shady Lane | 15:00 | 11:00 |  | 3600 | 42 | 236.8 | 3561 | 41 | 0 | 0.27
79466858 | 154 Shady Lane | 16:00 | 12:00 | YES | 3598 | 35 | 46.2 | 3598 | 35 | 0 | 0
79466858 | 154 Shady Lane | 17:00 | 13:00 | YES | 3600 | 20 | 48.8 | 3600 | 20 | 0 | 0
79466858 | 154 Shady Lane | 18:00 | 14:00 | YES | 3600 | -2 | 50.5 | 3600 | -2 | 0 | 0
79466858 | 154 Shady Lane | 19:00 | 15:00 | YES | 3600 | -23 | 49.7 | 3600 | -23 | 0 | 0

## Live Verification 8-29
Live re-verification, 2026-08-29
Register onset dating and a quiet-period residual re-screen, both pulled live on 8/29. The re-screen uses ordinary overnight quiet samples - no water shutoff required - which is the fleet-wide method proposed off the back of this investigation.
Register daily deltas (gal/day), pulled live 8/29
Device | Lot | Baseline | Onset | 8/24 | 8/25 | 8/26 | 8/27 | 8/28 | 8/29 | Cumulative
79461768 | 21 Maple | 48 gal/d (8/15-8/23) | 8/24 | 549 | 933 | 721 | 681 | 686 | 688 | 4,257 gal phantom 8/24-8/29, still accruing
70267966 | 40 Maple APT #5 | 105 gal/d (8/15-8/26) | 8/27 | 96 | 150 | 117 | 258 | 355 | 182 | 794 gal over 8/27-8/29 vs about 315 expected
79466007 | 126 Shady | 0 gal/d before 8/8 | leak 8/11, ended 8/24 | 0 | 0 | 0 | 0 | 0 | 0 | 10,698 gal leak 8/11-8/23, then zero every day
75367100 | 5033 Spruce | 2,664 gal 8/17-8/23 | dropped 8/24 | 81 | 45 | 140 | 60 | 49 |  | 375 gal 8/24-8/28; no report on 8/29
77054957 | 40 Maple APT #2 | 0 since wipe | wiped 5/29 | 0 | 0 | 0 | 0 | 0 | 0 | flat zero; meter itself screens clean
70269798 | 40 Maple APT #3 | 0 | failedCal | 0 | 0 | 0 | 0 | 0 | 0 | flat zero; no tofNorm since 8/5
Quiet-period residual re-screen (48 h to 8/29, no shutoff required)
Device | Lot | Quiet samples | tofNorm median | sd | gpm equivalent | Verdict | State on 8/27
75362887 | 66 Shady Lane | 0 |  |  |  | no data | zero samples
75364586 | 103 Shady Lane | 46624 | -25 | 73.7 | -0.0056 | OK - clean | noneventMode=FALSE, unassessable
75364883 | 5019 Spruce Lane | 0 |  |  |  | no data | zero samples
79455422 | 76 Shady Lane | 50000 | 6 | 38 | 0.0013 | OK - clean | zero samples
79454037 | 58 Shady Lane | 39177 | -145 | 71.4 | -0.0323 | OK - clean | zero samples
79461115 | 15 Maple Lane | 47139 | 4 | 77.1 | 0.0007 | OK - clean | only 82 samples
75366938 | 29 Maple Lane | 0 |  |  |  | no data | only 132 samples
70269798 | 40 Maple Lane APT #3 | 0 |  |  |  | no data | zero samples
75369098 | 5013 Spruce Lane | 0 |  |  |  | no data | noneventMode=FALSE
79459895 | 83 Shady Lane | 0 |  |  |  | no data | zero samples

## Method and Caveats
Method, conversions and caveats
Data source | ThingsBoard REST, device timeseries. Per-device raw samples saved in session f39664e0 scratchpad (d0827/*.json, shady_shutdown.json).
Why 8/27 is authoritative | recordNoneventFlow was set at GROUP level on Shady Lane MHP-Cust, so meters recorded tofNorm/flowRate continuously at 1 Hz instead of only inside detected events. That yields about 14,400 samples per device across the water-off block - a real zero-flow reference.
Attribute uptake | The DEVICE-scope attribute still reads 'unset' because it was set at group level; the reliable check is the noneventMode telemetry key. 30 of 36 devices reported noneventMode=true. 103 Shady and 5013 Spruce reported FALSE. 66 Shady and 58 Shady never reported it.
Confirmed water-off window | 8/27 16:00-20:00 UTC (12:00-16:00 EDT). Established from the data, not the clock: 8 of 9 meters with full-window continuous coverage integrate exactly 0.0 gal above 0.3 gpm for those four hours. This does not match the stated 9:00-13:00 exactly - the valve appears to have closed later than planned, or the stated times were approximate.
8/22 window is unreliable | On 8/22 the meters were in event-only mode, so tofNorm exists only when the meter believed water was moving - it cannot serve as a zero-flow reference. The window was inferred from the event ramp. Every bias figure derived from 8/22 is RETRACTED, including the -0.21 gpm attributed to 126 Shady and the -0.079 attributed to 21 Maple.
Transition threshold | 5-minute bin medians; a transition is logged at >= 250 counts of bin-to-bin shift. That is roughly 5x the healthy quiet-noise sd (39-46 counts) and about 0.056 gpm on 3/4 inch pipe. Bins with fewer than 5 samples are skipped.
Counts to gpm conversion | Empirical slopes fitted from tofNorm vs flowRate on flowing samples: 4,495 counts per gpm on 3/4 inch, 5,664 on 1/2 inch. Sign tracks install orientation. These are engineering approximations - confirm the scale on the bench before quoting percentages to a customer.
tofNorm is offset-corrected | tofNorm already has the meter's committed offset subtracted, so with no water it should read about zero. A non-zero quiet baseline IS the offset error.
Best fault discriminator | tofNorm standard deviation during any quiet period: 39-46 counts on healthy meters versus 1,648-1,765 on the broken ones. Combined with rejPct this works as a fleet-wide screen from ordinary overnight telemetry - no water shutoff required.
Register onset dates | Re-verified live on 8/29. 21 Maple: 48 gal/day baseline, then +549, +933, +721, +681, +686, +688 on 8/24-8/29 = 4,257 gal of phantom water and still climbing. 126 Shady: 10,698 gal over 8/11-8/23, then zero every day 8/24-8/29. See the Live Verification sheet.
Open housekeeping | recordNoneventFlow is still ON at the Shady Lane group level. It should be reverted once collection is complete - this is the attribute that filled device 75368777's flow ring and caused the session storm.
Not covered here | PEX 3/4 inch L-factor 2.27 remains unvalidated (pending Wyse fit); if the fitted value is lower, the whole site reads low proportionally. Metered-lot coverage versus the master meter is also unresolved - only 36 lots are metered.
Generated | 2026-08-30 14:38 local - Shady Lane MHP-Cust under-registration investigation